SECTION 02530 SANITARY SEWER

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

This section includes sanitary sewer piping and related appurtenances from connection to main to within 5 feet of outside building limits.

Pipe and fittings.

Non-pressure and pressure couplings.

Expansion joints and deflection fittings.

Backwater valves.

Cleanouts.

Encasement for piping.

Manholes.

REFERENCE STANDARDS

American Society for Testing and Materials (ASTM)

A746 - Standard Specification for Ductile Iron Gravity Sewer Pipe

D3034 – Standard Specification for Type PSM Poly Vinyl Chloride (PVC) Sewer Pipe and Fittings

F477 - Standard Specification for Elastomeric Seals (Gaskets) for Joining Plastic Pipe

F696 - Standard Specification for Poly Vinyl Chloride (PVC) Large-Diameter Plastic Gravity Sewer Pipe and Fittings

C476 - Standard Specification for Grout for Masonry

C443 - Standard Specification for Joints for Circular Concrete Sewer and Culvert Pipe, Using Rubber Gaskets

C923 - Standard Specification for Resilient Connectors Between Reinforced Concrete Manhole Structures, Pipes and Laterals

D2321 - Standard Practice for Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity-Flow Applications

D478 - Standard Specifications for Precast Reinforced Concrete Manhole Sections

C969 - Standard Practice for Infiltration and Exfiltration Acceptance Testing of Installed Precast Concrete Sewer Lines

American Society of Sanitary Engineers (ASSE)

American National Standards Institute (ANSI)

American Concrete Institute (ACI)

318 - Code Requirements for Structural Plain Concrete

National Sanitation Foundation (NSF)

American Water Works Association (AWWA)

C110 - Ductile-Iron and Gray-Iron Fittings, 3 in through 48 in (75 mm through 1200 mm), for Water and Other Liquids (revision of ANSI/AWWA C110/A21.10-93)

C1111 - Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings C153 - Ductile-Iron Compact Fittings, 3 in. through 24 in. (76 mm Through 610 mm) and 54 in. through 64 in. (1,400 mm Through 1,600 mm), for Water Service (revision of ANSI/AWWA C153/A21.53-94).

C600 - Installation of Ductile-Iron Water Mains and Their Appurtenances (revision of ANSI/AWWA C600-93)

C150 - ANSI Standard for Thickness Design of Ductile Iron Pipe

C151 – ANSI Standard for Ductile Iron Pipe

C153 – ANSI Standard for Ductile Iron Pipe Compact Fittings

Federal Specifications

SS-S-00210 - Sealing Compound Preformed Plastic for Pipe Joints

Uni-Bell PVC Pipe Association

UNI-B-6  -  Low-Pressure Air Testing of Installed Sewer Pipe

SUBMITTALS

Conformance Submittal:  The General Contractor and the Subcontractor shall execute the Conformance Submittal(s) at the end of this Section.

Field inspection, testing and quality-control reports.

Sanitary Sewer Certification Form (signed by the Engineer, General Contractor and Utility Contractor) at the end of this Section.

DELIVERY, STORAGE, AND HANDLING

Do not store pipe, and fittings in direct sunlight.

Protect pipe, pipe fittings, and seals from dirt and damage.

Handle manholes according to manufacturer's written rigging instructions.

PROJECT CONDITIONS

Coordination and Fees:

Contractor shall comply with requirements of the regulatory authorities having jurisdiction including tapping of sewer mains, installation and testing.

Contractor shall be responsible for obtaining and payment of all tap and construction permit fees associated with this Section.

Contractor to install all sanitary sewer lines and appurtenances as shown on the drawings to within 5 feet of building limits. If the Contractor’s work terminates at a connection point where work by others is complete, the Contractor shall make the connection. If future connections are required by others, the Contractor shall install plugging and marking as necessary to identify and locate the work.

Interruption of Existing Sanitary Sewerage Service:  Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:

Notify Owner no fewer than two days in advance of proposed interruption of service.

Do not proceed with interruption of service without Owner’s written permission.

PRODUCTS

DUCTILE-IRON, GRAVITY SEWER PIPE AND FITTINGS

Pipe:  ASTM A 746, for push-on joints.

Standard Fittings:  AWWA C110, ductile or gray iron, for push-on joints.

Compact Fittings:  AWWA C153, ductile iron, for push-on joints.

Gaskets:  AWWA C111, rubber.

PVC PIPE AND FITTINGS

Performance Requirements:

Gravity Flow Non-Pressure Piping Pressure Ratings: at least equal to system test pressure.

Force-Main Pressure Ratings: at least equal to system operating pressure but not less than 150 psig.

PVC Gravity Sewer Piping:

12 Inch and Smaller PVC Pipe and Fittings:  ASTM D 3034, SDR, PVC gravity sewer pipe with bell-and-spigot ends and with integral ASTM F 477, elastomeric seals for gasketed joints.

15 Inch and Larger PVC Pipe and Fittings: ASTM F 679, SDR 35, Type T-1 wall thickness, PVC gravity sewer pipe with bell-and-spigot ends and with integral ASTM F 477, elastomeric seals for gasketed joints.

NONPRESSURE-TYPE TRANSITION COUPLINGS

Comply with ASTM C 1173, elastomeric, sleeve-type, reducing or transition coupling, for joining underground nonpressure piping.  Include ends of same sizes as piping to be joined and corrosion-resistant-metal tension band and tightening mechanism on each end.

Sleeve Materials:

For Plastic Pipes:  ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

For Dissimilar Pipes:  ASTM D 5926, PVC or other material compatible with pipe materials being joined.

Unshielded, Flexible Couplings:

CLEANOUTS

Cleanouts shall be provided on sanitary sewer service laterals at no more than 100’ on center. Exterior cleanout plug shall be level with adjacent grade and provided with a 2’ x 2’ x 6” thick concrete apron as shown on the Drawings.

Cast-Iron Cleanouts:

Basis-of-Design Product:  Subject to compliance with requirements, provide US Foundry cover USF 7621 or equal product as indicated on Drawings.

Description:  ASME A112.36.2M, round, gray-iron housing with clamping device and round, secured, scoriated, gray-iron cover.  Include gray-iron ferrule with inside calk or spigot connection and countersunk, tapered-thread, brass closure plug.

Top-Loading Classification(s):  Heavy Duty.

Sewer Pipe Fitting and Riser to Cleanout:  ASTM A 74, Service class, cast-iron soil pipe and fittings.

PVC Cleanouts:

Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on Drawings.

Description:  PVC body with PVC threaded plug.  Include PVC sewer pipe fitting and riser to cleanout of same material as sewer piping.

ENCASEMENT FOR PIPING

Standard:  ASTM A 674 or AWWA C105.

Material:  high-density, cross-laminated polyethylene film of 0.004-inch (0.10-mm) minimum thickness.

Form:  Sheet.

Color:  Black.

MANHOLES

Standard Precast Concrete Manholes:

Description:  ASTM C 478 (ASTM C 478M), precast, reinforced concrete, of depth indicated, with provision for rubber gasketed joints and rubber pipe boots.

Inside Diameter:  48 inches (1200 mm) minimum unless otherwise indicated.

Ballast:  Increase thickness of precast concrete sections or add concrete to base section, as required to prevent flotation.

Base Section:  8-inch (175-mm) minimum thickness for floor slab and 5-inch (125-mm) minimum thickness for walls and base riser section; with separate base slab or base section with integral floor.

Riser Sections:  5-inch (125-mm) minimum thickness, of length to provide depth indicated.

Top Section:  Eccentric-cone type unless concentric-cone or flat-slab-top type is indicated; with top of cone of size that matches grade rings.

Gasket:  ASTM C 443, rubber (when required by local authority having jurisdiction).

Resilient Pipe Connectors:  ASTM C 923 (ASTM C 923M), cast or fitted into manhole walls, for each pipe connection.

Steps:  Individual FRP steps wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step.  Cast or anchor steps into sidewalls at 16-inch (400-mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than 42 inches (1050 mm).

Grade Rings (if required):  Reinforced-concrete rings, 6- to 9-inch (150- to 225-mm) total thickness, with diameter matching manhole frame and cover, and with height as required to adjust manhole frame and cover to indicated elevation and slope.

Pipe Connectors: ASTM C 923, resilient, of size required for each pipe connecting to base section.

Joints of the manhole sections shall be tongue and groove filled with approved preformed butyl rubber base sealing compound conforming to Federal Specifications SS-S210A, Type 1, and Rope Form.

Designed Precast Concrete Manholes:

Description:  ASTM C 913; designed according to ASTM C 890 for A-16 (ASSHTO HS20-44), heavy-traffic, structural loading; of depth, shape, and dimensions indicated, with provision for sealant joints.

Ballast:  Increase thickness of one or more precast concrete sections or add concrete to manhole as required preventing flotation.

Joint Sealant:  ASTM C 990 (ASTM 990M), bitumen or butyl rubber.

Resilient Pipe Connectors:  ASTM C 923 (ASTM C 923M), cast or fitted into manhole walls, for each pipe connection.

Steps:  Individual FRP steps or wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step.  Cast or anchor steps into sidewalls at 16-inch (400-mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than 42 inches (1050 mm).

Grade Rings:  Reinforced-concrete rings, 6- to 9-inch (150- to 225-mm) total thickness, with diameter matching manhole frame and cover, and with height as required to adjust manhole frame and cover to indicated elevation and slope.

Manhole Frames and Covers:

Description:  Ferrous; 24-inch (610-mm) ID by 7- to 9-inch (175- to 225-mm) riser, with 4-inch- (100-mm-) minimum-width flange and 26-inch- (660-mm-) diameter cover.  Include indented top design with 2 inch high lettering cast into cover, with the words "SANITARY SEWER." Cover must be bolted (to prevent theft).

Standard manhole frame and cover shall conform to the standard detail of the regulatory authorities having jurisdiction for the project. Otherwise manhole frames and covers shall be as detailed on the Drawings.

CONCRETE

General:  Cast-in-place concrete complying with ACI 318, ACI 350/350R (ACI 350M/350RM), and the following:

Cement:  ASTM C 150, Type II.

Fine Aggregate:  ASTM C 33, sand.

Coarse Aggregate:  ASTM C 33, crushed gravel.

Water:  Potable.

Portland Cement Design Mix:  4000 psi (27.6 MPa) minimum, with 0.45 maximum water/cementitious materials ratio.

Reinforcing Fabric:  ASTM A 185/A 185M, steel, welded wire fabric, plain.

Reinforcing Bars:  ASTM A 615/A 615M, Grade 60 (420 MPa) deformed steel.

Manhole Channels and Benches:  Factory or field formed from concrete.  Portland cement design mix, 4000 psi (27.6 MPa) minimum, with 0.45 maximum water/cementitious materials ratio.  Include channels and benches in manholes.

Channels:  Concrete invert, formed to same width as connected piping, with height of vertical sides to three-fourths of pipe diameter.  Form curved channels with smooth, uniform radius and slope.

Invert Slope:  2 percent through manhole.

Benches:  Concrete, sloped to drain into channel.

Slope:  4 percent.

Ballast and Pipe Supports:  Portland cement design mix, 3000 psi (20.7 MPa) minimum, with 0.58 maximum water/cementitious materials ratio.

Reinforcing Fabric:  ASTM A 185/A 185M, steel, welded wire fabric, plain.

Reinforcing Bars:  ASTM A 615/A 615M, Grade 60 (420 MPa) deformed steel.

EXECUTION

EARTHWORK

Excavating, trenching, and backfilling are specified in Division 2 Section "Earthwork".

PIPING INSTALLATION

General Locations and Arrangements:  Drawing plans and details indicate general location and arrangement of underground sanitary sewer piping.  Location and arrangement of piping layout take into account design considerations.  Install piping as indicated, to extent practical.  Where specific installation is not indicated, follow piping manufacturer's written instructions.

Install piping beginning at low point, true to grades and alignment indicated with unbroken continuity of invert.  Place bell ends of piping facing upstream.  Install gaskets, seals, sleeves, and couplings according to manufacturer's written instructions for using lubricants, cements, and other installation requirements.

Clear interior of piping and structures of dirt and deleterious materials as work progresses. Place plug in end of incomplete piping at end of day and work stops for greater than 24 hours. Flush piping between manholes and other structures to remove collected debris when needed.

Install manholes for changes in direction unless fittings are indicated.  Use fittings for branch connections unless direct tap into existing sewer is indicated.

Install proper size increasers, reducers, and couplings where different sizes or materials of pipes and fittings are connected.  Reducing size of piping in direction of flow is prohibited.

Install gravity-flow piping to within 5 feet of the building limits of sizes and in locations shown on the Drawings. Terminate piping as specified.

When installing pipe under streets or other obstructions that cannot be disturbed, use pipe-jacking process of micro tunneling.

Install gravity-flow, nonpressure, drainage piping according to the following:

Install piping pitched down in direction of flow, at slope shown on the Drawings, and at a minimum slope of 1 percent for 6 inch diameter pipe and 0.5 percent for 8 diameter inch pipes unless otherwise indicated.

Install piping with 36-inch (915-mm) minimum cover.

Install ductile-iron, gravity sewer piping according to ASTM A 746.

Install PVC gravity sewer piping according to ASTM D 2321 and ASTM F 1668.

Install force-main, pressure piping according to the following:

Install piping with restrained joints at tee fittings and at horizontal and vertical changes in direction.  Use corrosion-resistant rods, pipe or fitting manufacturer's proprietary restraint system, or cast-in-place-concrete supports or anchors.

Install piping with 36-inch (915-mm) minimum cover.

Install ductile-iron special fittings according to AWWA C600.

Install PVC pressure piping according to AWWA M23 or to ASTM D 2774 and ASTM F 1668.

If indicated on Drawings install corrosion-protection piping encasement over the following underground metal piping according to ASTM A 674 or AWWA C105:

Ductile-iron pipe and fittings.

Expansion joints and deflection fittings.

Clear interior of piping and manholes of dirt and superfluous material as work progresses.  Maintain swab or drag in piping, and pull past each joint as it is completed.  Place plug in end of incomplete piping at end of day and when work stops.

PIPE JOINT CONSTRUCTION

Join gravity-flow, nonpressure, drainage piping according to the following:

Join ductile-iron, gravity sewer piping according to AWWA C600 for push-on joints.

Join PVC gravity sewer piping according to ASTM D 2321 and ASTM D 3034 for elastomeric-seal joints or ASTM D 3034 for elastomeric-gasket joints.

Join dissimilar pipe materials with nonpressure-type, flexible or rigid couplings.

Join force-main, pressure piping according to the following:

Join PVC pressure piping according to AWWA M23 for gasketed joints.

Pipe couplings, expansion joints, and deflection fittings with pressure ratings at least equal to piping rating may be used in applications below unless otherwise indicated.

Use non-pressure flexible couplings where required to join gravity-flow, nonpressure sewer piping unless otherwise indicated.

Shielded flexible couplings for pipes of same or slightly different OD.

Unshielded, increaser/reducer-pattern, flexible couplings for pipes with different OD.

Ring-type flexible couplings for piping of different sizes where annular space between smaller piping's OD and larger piping's ID permits installation.

Use pressure pipe couplings for force-main joints.

MANHOLE INSTALLATION

General:  Install manholes complete with appurtenances and accessories indicated.

Install precast concrete manhole sections with sealants according to ASTM C 891.

Install FRP manholes according to manufacturer's written instructions.

Form continuous concrete channels and benches between inlets and outlet.

Set tops of frames and covers flush with finished surface of manholes that occur in pavements.  Set tops 3 inches (76 mm) above finished surface elsewhere unless otherwise indicated.

CONCRETE PLACEMENT

Place cast-in-place concrete according to ACI 318.

BACKWATER VALVE INSTALLATION (If used)

Install horizontal-type backwater valves in piping manholes or pits.

Install combination horizontal and manual gate valves in piping and in manholes.

Install terminal-type backwater valves on end of piping and in manholes.  Secure units to sidewalls.

CLEANOUT INSTALLATION

Install cleanouts and riser extensions from sewer pipes to cleanouts at grade.  Use cast-iron soil pipe fittings in sewer pipes at branches for cleanouts, and use cast-iron soil pipe for riser extensions to cleanouts.  Install piping so cleanouts open in direction of flow in sewer pipe.

Use Heavy-Duty, top-loading classification cleanouts in vehicle-traffic and truck service areas.

Set cleanout frames and covers in cast-in-place-concrete, 24 by 24 by 6 inches (600 by 600 by 150 mm) deep.  Set with tops flush with surrounding grade.

Set cleanout frames and covers in concrete pavement and roads with tops flush with pavement surface.

CONNECTIONS

Connect nonpressure, gravity-flow drainage piping to building's sanitary building drains specified in Division 15 Section "Sanitary Waste and Vent Piping."

Connect force-main piping to building's sanitary force mains specified in Division 15 Section "Sanitary Waste and Vent Piping." Terminate piping where indicated.

Make connections to existing piping and underground manholes.

Use commercially manufactured wye fittings for piping branch connections.  Remove section of existing pipe, install wye fitting into existing piping, and encase entire wye fitting plus 6-inch (150-mm) overlap with not less than 6 inches (150 mm) of concrete with 28-day compressive strength of 3000 psi (20.7 MPa).

Make branch connections from side into existing piping, NPS 4 to NPS 20 (DN 100 to DN 500).  Remove section of existing pipe, install wye fitting into existing piping, and encase entire wye with not less than 6 inches (150 mm) of concrete with 28-day compressive strength of 3000 psi (20.7 MPa).

Make branch connections from side into existing piping, NPS 21 (DN 525) or larger, or to underground manholes by cutting opening into existing unit large enough to allow 3 inches (76 mm) of concrete to be packed around entering connection.  Cut end of connection pipe passing through pipe or structure wall to conform to shape of and be flush with inside wall unless otherwise indicated.  On outside of pipe or manhole wall, encase entering connection in 6 inches (150 mm) of concrete for minimum length of 12 inches (300 mm) to provide additional support of collar from connection to undisturbed ground.

Use concrete that will attain a minimum 28-day compressive strength of 3000 psi (20.7 MPa) unless otherwise indicated.

Use epoxy-bonding compound as interface between new and existing concrete and piping materials.

Protect existing piping and manholes to prevent concrete or debris from entering while making tap connections.  Remove debris or other extraneous material that may accumulate.

Connect to grease oil and sand interceptors specified in Division 2 Section "Sanitary Sewer."

CLOSING ABANDONED SANITARY SEWER SYSTEMS

The Contractor shall be responsible for removal and/or relocation of existing utilities as necessary, whether shown or not shown on the Drawings. At locations where conflicts occur with proposed sanitary sewer improvements, removal and relocation shall be at no additional cost to the Owner.

Abandoned Piping:  Close and grout fill open ends of abandoned underground piping indicated to remain in place.  Include closures strong enough to withstand hydrostatic and earth pressures that may result after ends of abandoned piping have been closed.  Use either procedure below:

Close open ends of piping with at least 8-inch- (203-mm-) thick, brick masonry bulkheads.

Close open ends of piping with threaded metal caps, plastic plugs, or other acceptable methods suitable for size and type of material being closed.  Do not use wood plugs.

Abandoned Manholes:  Excavate around manhole as required and use either procedure below:

Remove manhole and close open ends of remaining piping.

Remove top of manhole down to at least 36 inches (915 mm) below final grade.  Fill to within 12 inches (300 mm) of top with gravel, or compacted dirt.  Fill to top with concrete.

Backfill to grade according to Division 2 Section “Earthwork”.

      - IDENTIFICATION

        - Materials and their installation are specified in Division 2 Section "Earthwork." Arrange for installation of green warning tapes directly over piping and at outside edges of underground manholes.

          - Use warning tape or detectable warning tape over ferrous piping.

          - Use detectable warning tape over nonferrous piping and over edges of underground manholes.

      - FIELD QUALITY CONTROL

        - Inspect interior of piping to determine whether line displacement or other damage has occurred.  Inspect after approximately 24 inches (600 mm) of backfill is in place, and again at completion of Project.

          - Submit separate report for each system inspection.

          - Defects requiring correction include the following:

            - Alignment:  Less than full diameter of inside of pipe is visible between structures.

            - Deflection:  Flexible piping with deflection that prevents passage of ball or cylinder of size not less than 95 percent of piping diameter.

            - Damage:  Crushed, broken, cracked, or otherwise damaged piping.

            - Infiltration:  Water leakage into piping.

            - Exfiltration:  Water leakage from or around piping.

          - Replace defective piping using new materials, and repeat inspections until defects are within allowances specified.

          - Re-inspect and repeat procedure until results are satisfactory.

        - Test new piping systems, and parts of existing systems that have been altered, extended, or repaired, for leaks and defects.

          - Do not enclose, cover, or put into service before inspection and approval.

          - Test completed piping systems according to requirements of authorities having jurisdiction.

          - Schedule tests and inspections by authorities having jurisdiction with at least 24 hours' advance notice.

          - Submit separate report for each test to General Contractor within 2 days of test.

          - If authorities having jurisdiction do not have published procedures, perform tests as follows:

            - Hydrostatic Tests:  Test sanitary sewerage according to requirements of authorities having jurisdiction and the following:

              - Fill sewer piping with water.  Test with pressure of at least 10-foot (3-m) head of water, and maintain such pressure without leakage for at least 15 minutes.

              - Close openings in system and fill with water.

              - Purge air and refill with water.

              - Disconnect water supply.

              - Test and inspect joints for leaks.

              - Allowable leakage is a maximum of 50 gal. Per inch of nominal pipe size per mile of pipe per day.

              - Option: Test ductile iron piping according to AWWA C600, Section “Hydrostatic Testing”. Use test pressure of at least 10 psig.

          - Air Tests:  Test sanitary sewerage according to requirements of authorities having jurisdiction, UNI-B-6, and the following:

            - Option:  Test plastic gravity sewer piping according to ASTM F 1417.

          - Force Main:  Perform hydrostatic test after thrust blocks, supports, and anchors have hardened.  Test at pressure not less than 1-1/2 times the maximum system operating pressure, but not less than 150 psig (1035 kPa).

            - PVC Piping:  Test according to AWWA M23, "Testing and Maintenance" Chapter.

          - Manholes:  Perform hydraulic test according to ASTM C 969 (ASTM C 969M).

        - Leaks and loss in test pressure constitute defects that must be repaired.

        - Replace leaking piping using new materials, and repeat testing until leakage is within allowances specified.

      - CLEANING

        - Clean dirt and superfluous material from interior of piping flush with potable water.

END OF SECTION 02530

# CONFORMANCE SUBMITTAL

# SECTION 02530 – SANITARY SEWER

Lowe’s of ________________________________________________________________________

(City, State)

General Contractor:	________________________________________________________________

(Company Name, Phone Number)

_______________________________________________________________

(Address)

Sub-Contractor:		________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

___________________________________________

The following products have been selected (check one box) for use in this project from the list of acceptable products specified:

Piping Materials:

Ductile-Iron Pipe, ASTM A746

Polyvinyl Chloride (PVC) Pipe, ASTM D3034, SDR 35, Elastomeric Gasket Joints ASTM F477

Other per AHJ:

Manholes:

Precast with Cored or Cast Holes with Properly Sized Boots

Other per AHJ:

I represent to Lowe’s that the products selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the contract documents. If noncompliance is discovered the General Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and specifications.  Immediately or as directed by Lowe’s the work shall be completed without additional cost to the Lowe’s and / or the contract.

Sub-Contractor:		________________________________________________________________

(Signature of the Authorized Agent of the Sub-Contractor)		Date

________________________________________________________________

(Print Name of the Authorized Agent of the Sub-Contractor)

General Contractor:	________________________________________________________________

(Signature of the Authorized Agent of the General Contractor)		Date

________________________________________________________________

(Print Name of the Authorized Agent of the General Contractor)

SANITARY SEWER CERTIFICATION FORM

| ## Project |  |
| --- | --- |
| Date |  |
| Engineer |  |
| General Contractor |  |
| Utility Contractor |  |
| Lowe’s Const. Mgr. |  |

# ENGINEER CERTIFICATION (If required)

I certify that the sanitary sewer system for the above referenced project has been installed and tested in accordance with local code and Lowe’s Plans and Specifications dated 				.

Engineer

Registration No.					 	Affix Seal Here (not valid unless sealed)

Date

# GENERAL CONTRACTOR CERTIFICATION (Required)

I certify that the sanitary sewer system for the above referenced project has been installed and tested in accordance with local code and Lowe’s Plans and Specifications dated 				.

General Contractor

License No.

Date

# UTILITY CONTRACTOR CERTIFICATION (Required)

I certify that the sanitary sewer system for the above referenced project has been installed and tested in accordance with local code and Lowe’s Plans and Specifications dated 				.

Utility Contractor

License No.

Date

- * Submit this certification form with test results, local certificates, etc.