SECTION 02630 – STORM UTILITY DRAINAGE PIPING

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 2 Specification Sections apply to this Section.

SUMMARY

Section Includes:

Pipe and fittings.

Nonpressure transition couplings.

Pressure pipe couplings.

Expansion joints and deflection fittings.

Backwater valves.

Cleanouts.

Drains.

Encasement for piping.

Manholes.

Channel drainage systems.

Catch basins.

Stormwater inlets.

Stormwater detention structures.

Pipe outlets.

Dry wells.

Stormwater disposal systems.

STANDARDS

        - American Society For Testing and Materials (ASTM)

A185 – Standard Specification for Steel Welded Wire Reinforcement, Plain, for Concrete

A615 – Standard Specification for Deformed and Plain Carbon-Steel Bars for Concrete Reinforcement

A760 – Standard Specification for Corrugated Steel Pipe, Metallic-Coated, for Sewers and Drains

A762 – Standard Specification for Corrugated Steel Pipe, Polymer Precoated for Sewers and Drains

A798 – Standard Specification for Installing Factory-Made Corrugated Steel Pipe for Sewers and Other Applications

B745 – Standard Specification for Corrugated Aluminum Pipe for Sewers and Drains

B788 – Standard Practice for Installing Factory-Made Corrugated Aluminum Culverts and Storm Sewer Pipe

A761– Standard Specification for Corrugated Steel Structural Plate, Zinc-Coated, for Field-Bolted Pipe, Pipe-Arches, and Arches

A807 – Standard Practice for Installing Corrugated Steel Structural Plate Pipe for Sewers and Other Applications

A964 – Standard Specification for Corrugated Steel Box Culverts

B746 – Standard Specification for Corrugated Aluminum Alloy Structural Plate for Field-Bolted Pipe, Pipe-Arches, and Arches

B789 – Standard Practice for Installing Corrugated Aluminum Structural Plate Pipe for Culverts and Sewers

B864 – Standard Specification for Corrugated Aluminum Box Culverts

C76 – Standard Specification for Reinforced Concrete Culvert, Storm Drain, and Sewer Pipe

C443 – Standard Specification for Joints for Concrete Pipe and Manholes, Using Rubber Gaskets

C478 – Standard Specification for Precast Reinforced Concrete Manhole Sections

C507 – Standard Specification for Reinforced Concrete Elliptical Culvert, Storm Drain, and Sewer Pipe

C913 – Precast Concrete Water and Wastewater Structures

C923 – Standard Specification for Resilient Connectors Between Reinforced Concrete Manhole Structures, Pipes, and Laterals

C990 – Standard Specification for Joints for Concrete Pipe, Manholes, and Precast Box Sections Using Preformed Flexible Joint Sealants

C1107 – Standard Specification for Packaged Dry, Hydraulic-Cement Grout (Nonshrink)

C1433 – Standard Specification for Precast Concrete Monolithic Box Sections for Culverts, Storm Drains, and Sewers

C1478 – Standard Specification for Storm Drain Resilient Connectors Between Reinforced Concrete Storm Sewer Structures, Pipes, and Laterals

C1479 – Standard Practice for Installation of Precast Concrete Sewer, Storm Drain, and Culvert Pipe Using Standard Installations

C1577 – Standard Specification for Precast Reinforced Concrete Monolithic Box Sections for Culverts, Storm Drains, and Sewers Designed According to AASHTO LRFD

C1675 – Practice for Installation of Precast Reinforced Concrete Monolithic Box Sections for Culverts, Storm Drains, and Sewers

D698-07e1 – Standard Test Methods for Laboratory Compaction Characteristics of Soil Using Standard Effort

D1056 – Standard Specification for Flexible Cellular Materials – Sponge or Expanded Rubber

F2306 – Standard Specification for 12 to 60 in. Annular Corrugated Profile-Wall Polyethylene Pipe and Fittings for Gravity-Flow Storm Sewer and Subsurface Drainage Applications

D2321 – Standard Practice for Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity-Flow Applications

D3034 – Standard Specification for Type PSM Poly(Vinyl Chloride) (PVC) Sewer Pipe and Fittings

D3212 – Standard Specification for Joints for Drain and Sewer Plastic Pipes Using Elastomeric Seals

F477 – Standard Specification for Elastomeric  Seals (Gaskets) for Joining Plastic Pipe

F794 – Standard Specification for Poly(Vinyl Chloride) (PVC) Profile Gravity Sewer Pipe and Fittings Based on Controlled Inside Diameter

F949 – Standard Specification for Poly(Vinyl Chloride) (PVC) Corrugated Sewer Pipe With a Smooth Interior and Fittings

F2418 – Standard Specification for Polypropylene (PP) Corrugated Wall Stormwater Collection Chambers

F2510 – Standard Specification for Resilient Connectors Between Reinforced Concrete Manhole Structures and Corrugated High Density Polyethylene Drainage Pipes

F2562 – Specification for Steel Reinforced Thermoplastic Ribbed Pipe and Fittings for Non-Pressure Drainage and Sewerage

C1504 – Standard Specification for Manufacture of Precast Reinforced Concrete Three-Sided Structures for Culverts and Storm Drains

        - American Association of State Highway and Transportation Officials (AASHTO)

M36 – Standard Specification for Corrugated Steel Pipe, Metallic-Coated, for Sewers and Drains

M167 – Standard Specification for Corrugated Steel Structural Plate, Zinc-Coated, for Field-Bolted Pipe, Pipe-Arches, and Arches

M196 – Standard Specification for Corrugated Aluminum Pipe for Sewers and Drains

M198 – Standard Specification for Joints for Concrete Pipe, Manholes, and Precast Box Sections Using Preformed Flexible Joint Sealants

M219 – Standard Specification for Corrugated Aluminum Alloy Structural Plate for Field-Bolted Pipe, Pipe-Arches, and Arches

M245 – Standard Specification for Corrugated Steel Pipe, Polymer-Precoated, for Sewers and Drains

M252 – Standard Specification for Corrugated Polyethylene Drainage Pipe

M274 – Standard Specification for Steel Sheet, Aluminum-Coated (Type 2), for Corrugated Steel Pipe

M288 – Standard Specification for Geotextile Specification for Highway Applications

M294 – Standard Specification for Corrugated Polyethylene Pipe, 12” through 60” Diameter

M43 – Standard Specification for Sizes of Aggregate for Road and Bridge Construction

M190 – Standard Specification for Bituminous-Coated Corrugated Metal Culvert Pipe and Pipe Arches

M199 – Standard Specification for Precast Reinforced Concrete Manhole Sections

AASHTO LRFD Bridge Design Specifications Sections 3 & 12

AASHTO LRFD Bridge Construction Specifications Sections 26, 27 and 30

AASHTO PP63 – Pipe Joint Selection for Highway Culvert and Storm Drains

        - American Water Works Association (AWWA)

C110 – Standard for Ductile-Iron and Gray-Iron Fittings

C111 – Standard for Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings

C151 – Standard for Ductile-Iron Pipe, Centrifugally Cast

        - American Concrete Institute (ACI)

301 – Specifications for Structural Concrete

318 – Building Code Requirements for Structural Concrete and Commentary

American Concrete Pipe Association

LRFD Fill Height Tables for Concrete Pipe

LRFD Fill Height Tables for Elliptical Concrete Pipe

Post Installation Evaluation and Repair of Installed Reinforced Concrete Pipe

Concrete Pipe and Box Culvert Installation Manual

SUBMITTALS

The General Contractor and the Subcontractor shall execute the Conformance Submittals at the end of this section:

Storm Drainage Conformance Submittal

Product Data:  For each type of product indicated.

Shop Drawings:

Manholes:  Include plans, elevations, sections, details, frames, and covers.

Catch basins stormwater inlets and dry wells.  Include plans, elevations, sections, details, frames, covers, and grates.

Stormwater Detention Structures:  Include plans, elevations, sections, details, frames, covers, and concrete design-mix reports.

Product Certificates:  For each type of cast-iron soil pipe and fitting, from manufacturer.

Field quality-control reports.

Markings:  Markings shall be provided on all products as specified in the product’s corresponding ASTM standard (i.e. date of manufacture, manufacturer name, product type, etc.)

Project Record Drawings: Accurately record as-built locations of pipe runs, connections, catch basins, cleanouts, top elevations, and invert elevations. Identify and describe unexpected variations of subsurface conditions and location of any utilities encountered.  Utility crossings shall be clearly labeled with size, type, invert, and clearance provided at utility crossing.

QUALITY ASSURANCE

All costs associated with re-inspection due to failures shall be paid for by the Contractor at no additional expense to the Owner. Owner reserves the right to direct any inspection that is deemed necessary. Contractor shall provide free access to site for inspection activities.

DELIVERY, STORAGE, AND HANDLING

Do not store plastic, pipe, and fittings in direct sunlight.

All pipe shall be protected against impact, shock and free fall, and only equipment of sufficient capacity and proper design shall be used in the handling of the pipe. Pipes and chambers shall not be rolled or dragged over any surface. The Contractor shall take necessary precautions to ensure the method used in lifting or placing the pipe or chambers does not induce stress fatigue in the pipe or chamber and the lifting device used uniformly distributes the weight of the pipe or chamber along the axis or circumference. Storage of pipe on the job shall be in accordance with the pipe manufacturer’s recommendations.

Protect pipe, pipe fittings, and seals from dirt and damage.

Damage to Pipe or Chambers:

Each length of pipe or chamber shall be inspected for defects and cracks before carefully being lowered into the trench.

Bituminous coated pipe shall be handled with special care and repair of damaged coating shall conform to AASHTO M190.

Pipe or chambers which are defective from any cause, including damage caused by handling, storage or any other reason as determined by the Owner to be not repairable, shall be unacceptable for installation and shall be replaced at no cost to the Owner and as directed by the Owner.

Pipe or chambers that are damaged or disturbed through any cause prior to acceptance of the work shall be repaired, realigned, or replaced as directed by the Owner at no expense to the Owner.

Handle manholes according to manufacturer's written rigging instructions.

Handle catch basins and stormwater inlets according to manufacturer's written rigging instructions.

PROJECT CONDITIONS

Removal/Relocation of Existing Utilities: The Contractor shall be responsible for removal and/or relocation of existing utilities, whether shown or not shown on the drawings, at locations where conflicts occur with proposed storm drainage improvements.  Removal and relocation shall be at no additional cost to the Owner.

Interruption of Existing Storm Drainage Service:  Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:

Notify Owner no fewer than seven days in advance of proposed interruption of service.

Do not proceed with interruption of service without Owner's written permission.

PRODUCTS

DUCTILE-IRON, CULVERT PIPE AND FITTINGS

Pipe:  ASTM A716, for push-on joints.

Standard Fittings:  AWWA C110, ductile or gray iron, for push-on joints.

Compact Fittings:  AWWA C153, for push-on joints.

Gaskets:  AWWA C111, rubber.

ALUMINIZED PIPE AND FITTINGS

Aluminized Steel Type 2 Corrugated Steel Pipe 2 (CMP):

Pipe for the specified diameter (rise x span for pipe-arches), gage and corrugation shall be made in conformance to ASTM A760 (AASHTO M36) and meet the material requirements of ASTM A929 (AASHTO M 274) for aluminized steel (Type 2).

Minimum thickness shall be 16 gage for pipe diameters 10-24 in., 14 gage for diameters 30-48 in. Stormwater detention systems only: 12 gage for diameters 54-96 in. and 10 gage for diameters 102 in. and larger, but not less than the diameter indicated on the drawings.

Pipe joining systems shall utilize corrugated bands to the width and thicknesses defined in ASTM A760 for aluminized (Type 2) steel. Band connectors shall also meet the requirements of ASTM A760. Where leakage is a concern the joining system shall incorporate gaskets meeting the material requirements defined in ASTM A760. Maximum permitted diameter for CMP storm drainage piping is 48 in.

CMP larger than 48 in. diameter is allowed for subsurface stormwater detention systems only.

HDPE PIPE AND FITTINGS

High Density Polyethylene Pipe (HDPE) Smooth Interior Pipe:

Pipe and Fittings: Shall conform to AASHTO M252, M294 and/or ASTM F2306 unless otherwise shown on the Drawings.

Bell and spigot joints shall meet the water tight requirements of ASTM D3212.

Maximum permitted diameter is 48 in.

See drawings for bedding details.

PVC PIPE AND FITTINGS

PVC Cellular-Core Piping:

PVC Cellular-Core Pipe and Fittings:  ASTM F891, Sewer and Drain Series, PS 50 minimum stiffness, PVC cellular-core pipe with plain ends for solvent-cemented joints.

Fittings:  ASTM D 3034, SDR 35, PVC socket-type fittings.

PVC Corrugated Sewer Piping:

Pipe:  ASTM F 949, and ASTM F 794 PVC, corrugated pipe with bell-and-spigot ends for gasketed joints.

Fittings:  ASTM F 949, PVC molded or fabricated, socket type.

Gaskets:  ASTM F 477, elastomeric seals with joints conforming to ASTM D3212

CONCRETE PIPE, BOX CULVERT SECTIONS, ELLIPTICAL PIPE AND FITTINGS

Reinforced-Concrete Pipe and Fittings:  Unless otherwise indicated on the drawings, provide drainage pipe meeting ASTM C76.

Where designated on the drawings, provide RCP with tongue-and-groove joints with a preformed flexible bitumen or butyl-rubber sealant meeting ASTM C990 to form a silt-tight joint.

Where designate on the drawings, provide RCP with bell-and spigot joints with a rubber gasket meeting ASTM C443 to form a leak-resistant joint.

Class III, unless otherwise indicated on the Drawings.

Precast Reinforced Concrete Monolithic Box Sections and Fittings:

Where designated on the drawings, provide RCB with ASTM C990 joints and preformed flexible  bitumen or butyl-rubber sealant to form a silt-tight joint.

Provide monolithic RCB sections to meet ASTM C1433 or ASTM C1577 for the span, rise, design fill height and live load condition indicated on the drawings.

Reinforced  Concrete Elliptical Pipe and Fittings:

Where designated on the drawings, provide elliptical pipe with ASTM C990 joints and preformed flexible bitumen or butyl-rubber sealant to form a silt-tight joint.

Provide elliptical pipe class as indicated on the drawings.

NONPRESSURE TRANSITION COUPLINGS

Comply with ASTM C1173, elastomeric, sleeve-type, reducing or transition coupling, for joining underground non-pressure piping.  Include ends of same sizes as piping to be joined, and corrosion-resistant-metal tension band and tightening mechanism on each end.

Sleeve Materials:

For Concrete Pipes:  ASTM C443 (ASTM C443M), rubber.

For Cast-Iron Soil Pipes:  ASTM C564, rubber.

For Fiberglass Pipes:  ASTM F477, elastomeric seal or ASTM D5926, PVC.

For Plastic Pipes:  ASTM F477, elastomeric seal or ASTM D5926, PVC.

For Dissimilar Pipes:  ASTM D5926, PVC or other material compatible with pipe materials being joined.

Unshielded, Flexible Couplings:

Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on the Drawings.

Shielded, Flexible Couplings:

Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on Drawings

Ring-Type, Flexible Couplings:

Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on Drawings

DRAINS

Sub Drains:

Shall be perforated PVC or HDPE unless otherwise indicated on the Drawings.  Installation shall be as shown on the drawings.

CLEANOUTS AND PLUGS

Installation shall be as shown on the details and at locations shown on the drawings.

All cleanouts shall have a 2’ x 2’ x 6” thick concrete apron.

ENCASEMENT FOR PIPING

Standard:  ASTM A674 or AWWA C105.

Material:  Linear low-density polyethylene film of 0.008 in. (0.20 mm) minimum thickness.

Form:  Sheet or tube.

Color:  Black.

      - MANHOLES

        - Standard Precast Concrete Manholes:

          - Description:  ASTM C478 (ASTM C478M) and AASHTO M199, precast, reinforced concrete, of depth indicated, with provision for sealant joints. Heavy-duty traffic rated in accordance with Department of Transportation Standards in which project is located.

          - Diameter:  48 in. (1200 mm) minimum unless otherwise indicated.

          - Ballast:  Increase thickness of precast concrete sections or add concrete to base section as required preventing flotation.

          - Base Section:  6 in. (150-mm) minimum thickness for manholes up to and including 48 in. in diameter and 8 in. for larger diameter manholes.

          - Riser Sections:  4 in. (102-mm) minimum wall thickness for 48 in. diameter manholes.  Larger diameter manholes shall have minimum wall thickness of one twelfth of the largest diameter of the riser or conical top.

          - Top Section:  Conical or flat slab top type, and top of cone of size that matches grade rings.

          - Joint Sealant:  ASTM C990 (ASTM C990M), bitumen or butyl rubber.

          - Grout:  ASTM C1107 (C1107M-08), non-shrink fluid grout for soil-tight pipe to manhole connection.

          - Resilient Pipe Connectors:  ASTM C923 (ASTM C923M), cast or fitted into manhole walls, for leak-resistant pipe to manhole connection.

          - Steps:  Individual FRP steps; FRP ladder; or ASTM A615/A615M, deformed, ½ in. (13 mm) steel reinforcing rods encased in ASTM D 4101, PP, wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step.  Cast or anchor steps into sidewalls at 16 in. (400 mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than 42 in. (1050 mm).

          - Grade Rings:  Reinforced-concrete rings shall have minimum wall thickness of one twelfth of the internal diameter, or 4 in., whichever is greater.  Grade rings shall match diameter and thickness of manhole conical riser.  Ring height shall be as required to adjust manhole frame and cover to indicated elevation and slope.

        - Designed Precast Concrete Manholes:

          - Description:  ASTM C913; designed according to ASTM C890 for A-16 (AASHTO HS20-44), heavy-traffic, structural loading; of depth, shape, and dimensions indicated, with provision for sealant joints.

          - Ballast:  Increase thickness of one or more precast concrete sections or add concrete to manhole as required preventing flotation.

          - Joint Sealant:  ASTM C990 (ASTM C990M), bitumen or butyl rubber.

          - Grout:  ASTM C1107 (C1107M-08), non-shrink fluid grout for soil-tight pipe to manhole connection.

          - Resilient Pipe Connectors:  ASTM C923 (ASTM C923M), cast or fitted into manhole walls, for leak-resistant pipe to manhole connection.

          - Steps:  Individual FRP steps; FRP ladder; or ASTM A615/A615M, deformed, ½ in. (13 mm) steel reinforcing rods encased in ASTM D 4101, PP, wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step.  Cast or anchor steps into sidewalls at 16 in. (400 mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than 42 in. (1050 mm).

          - Grade Rings:  Reinforced-concrete rings shall have minimum wall thickness of one twelfth of the internal diameter, or 4 in., whichever is greater.  Grade rings shall match diameter and thickness of manhole conical riser.  Ring height shall be as required to adjust manhole frame and cover to indicated elevation and slope.

        - Manhole Frames and Covers:

          - Description:  As shown on the Drawings, otherwise provide ferrous; 24 in. (610 mm) ID by 7 to 9 in. (175 to 225 mm) riser with 4 in. (102 mm) minimum width flange and 26 in. (660 mm) diameter security bolted cover.

          - Material:  ASTM A536, Grade 60-40-18 ductile iron unless otherwise indicated.

      - BEDDING AND BACKFILL MATERIAL

Bedding material placement and compaction shall be as specified by trenching and bedding details shown on the drawings.

Haunching, initial backfill, and final backfill material and compaction shall be as specified by trenching and bedding details shown on the drawings.  Material shall be placed per ASTM D698, and compacted in 8 in. (0.2 m) maximum lifts.

Where the foundation material is found to be of poor supporting value or of rock, the Owner may make minor adjustments in the location of the pipe to provide a more suitable foundation.  Where this is not practical, the foundation shall be conditioned by removing the existing foundation material by undercutting to the depth as directed by the geotechnical engineer and backfilling with either a suitable local material secured from unclassified excavation or borrow excavation at the nearest accessible location along the project, or foundation conditioning material consisting of crushed stone or gravel or a combination of sand and crushed stone or gravel approved by geotechnical engineer as being suitable for the purpose intended.  The selection of the type of backfill material to be used for foundation conditioning will be made by the geotechnical engineer.

      - CONCRETE

        - General:  Cast-in-place concrete according to ACI 318, ACI 350/350R (ACI 350M/350RM), and the following:

          - Cement:  ASTM C 150, Type II.

          - Fine Aggregate:  ASTM C33, sand.

          - Coarse Aggregate:  ASTM C33, crushed gravel.

          - Water:  Potable.

        - Portland Cement Design Mix:  (28 day compressive strength) 4000 psi (27.6 MPa) minimum, with 0.45 maximum water/cementitious materials ratio.

          - Reinforcing Fabric:  ASTM A185/A185M, steel, welded wire fabric, plain.

          - Reinforcing Bars:  ASTM A615/A615M, Grade 40 or 60 (420 MPa) deformed steel.

        - Manhole, Catch Basin, and Storm Inlet Channels and Benches:  Factory or field formed from concrete.  Portland cement design mix, 4000 psi (27.6 MPa) minimum, with 0.45 maximum water/cementitious materials ratio.  Include channels and benches in manholes.

          - Channels:  Concrete invert, formed to same width as connected piping, with height of vertical sides to three-fourths of pipe diameter.  Form curved channels with smooth, uniform radius and slope.

            - Invert Slope:  1 percent through manhole unless otherwise detailed on the Drawings.

          - Benches:  Concrete, sloped to drain into channel.

            - Slope:  4 percent unless otherwise detailed on the drawings.

        - Ballast and Pipe Supports:  Portland cement design mix, 3000 psi (20.7 MPa) minimum, with 0.58 maximum water/cementitious materials ratio.

          - Reinforcing Fabric:  ASTM A185/A185M, steel, welded wire fabric, plain.

          - Reinforcing Bars:  ASTM A615/A615M, Grade 60 (420 MPa) deformed steel.

      - CATCH BASINS

        - Standard Precast Concrete Catch Basins:

          - Description:  ASTM C478 (ASTM C478M), precast, reinforced concrete, heavy duty (H20), of depth indicated, with provision for sealant joints.

          - Base Section:  6 in. (150-mm) minimum thickness for manholes up to and including 48 in. in diameter and 8 in. for larger diameter manholes.

          - Riser Sections:  4 in. (102-mm) minimum wall thickness for 48 in. diameter manholes.  Larger diameter manholes shall have minimum wall thickness of one twelfth of the largest diameter of the riser or conical top.

          - Top Section:  Conical or flat slab top type, and top of cone of size that matches grade rings.

          - Joint Sealant:  ASTM C990 (ASTM C990M), bitumen or butyl rubber.

          - Grade Rings:  Reinforced-concrete rings shall have minimum wall thickness of one twelfth of the internal diameter, or 4 in., whichever is greater.  Grade rings shall match diameter and thickness of manhole conical riser.  Ring height shall be as required to adjust manhole frame and cover to indicated elevation and slope.

          - Steps:  Individual FRP steps; FRP ladder; or ASTM A615/A615M, deformed, ½ in. (13-mm) steel reinforcing rods encased in ASTM D4101, PP, wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step.  Cast or anchor steps into sidewalls at 16 in. (400-mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than 42 in. (1050 mm).

          - Grout:  ASTM C1107 (C1107M-08), non-shrink fluid grout for soil-tight pipe to catch basin connection.

          - Pipe Connectors:  ASTM C923 (ASTM C923M), resilient, of size required, for water-tight pipe connecting to base section.

        - Designed Precast Concrete Catch Basins:  ASTM C913, precast, reinforced concrete; designed according to ASTM C890 for A-16 (ASSHTO HS20-44), heavy-traffic, structural loading; of depth, shape, and dimensions indicated, with provision for joint sealants.

          - Joint Sealants:  ASTM C990 (ASTM C990M), bitumen or butyl rubber.

          - Grade Rings:  Reinforced-concrete rings shall have minimum wall thickness of one twelfth of the internal diameter, or 4 in., whichever is greater.  Grade rings shall match diameter and thickness of manhole conical riser.  Ring height shall be as required to adjust manhole frame and cover to indicated elevation and slope.

          - Steps:  Individual FRP steps; FRP ladder; or ASTM A615/A615M, deformed, ½ in. (13-mm) steel reinforcing rods encased in ASTM D 4101, PP, wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step.  Cast or anchor steps into sidewalls at 16 in. (40 mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than 42 in. (1050 mm).

          - Grout:  ASTM C1107 (C1107M-08), non-shrink fluid grout for soil-tight pipe to catch basin connection.

          - Pipe Connectors:  ASTM C923 (ASTM C923M), resilient, of size required, for leak-resistant pipe connecting to base section.

        - Grate and Frame: Per details shown on the drawings. Provide hood with stencil or casting “Dump No Waste – Drains to Waterways” or equal. Provide local casting if required. Provide 6 in. thick rectangular concrete apron, with 18 in. minimum width measured from the edge of structure frame to the end of the concrete apron, around all structure frames located in asphalt pavement areas. Provide saw cuts from each corner of the concrete apron to the frame of the structure as shown on the plan.

          - Rectangular Frames and Grates:  ASTM A536, Grade 60-40-18, ductile iron designed for A-16, heavy duty (H20) structural loading.  Include flat grate with small square or short-slotted drainage openings.

            - Size:  24 in. by 24 in. (610 by 610 mm) minimum unless otherwise indicated.

            - Grate Free Area:  Approximately 50 percent unless otherwise indicated.

          - Round, Manhole Type Frames and Grates:  ASTM A536, Grade 60-40-18, ductile iron designed for A-16, heavy duty (H20) structural loading.  Include 24 in. (610 mm) ID by 7 to 9 in. (175 to 225 mm) riser with 4 in. (102 mm) minimum width flange, and 26 in. (660 mm) diameter flat grate with small square or short-slotted drainage openings.

            - Grate Free Area:  Approximately 50 percent unless otherwise indicated.

      - STORMWATER INLETS

        - Curb Inlets:  Made with vertical curb opening of materials and dimensions according to the details shown on the Drawings.

        - Gutter Inlets:  Made with horizontal gutter opening of materials and dimensions according to the details shown on the Drawings. Include heavy-duty frames and grates.

        - Combination Inlets:  Made with vertical curb and horizontal gutter openings of materials and dimensions according to the details shown on the Drawings. Include heavy-duty frames and grates.

        - Frames and Grates:  Heavy duty and according to the details shown on the Drawings.

      - STORMWATER DETENTION STRUCTURES

        - Cast-in-Place Concrete, Stormwater Detention Structures:  Constructed of reinforced-concrete bottom, walls, and top; designed according to ASTM C890 for A-16 (AASHTO HS20-44), heavy-traffic, structural loading; of depth, shape, dimensions, and appurtenances indicated.

          - Ballast:  Increase thickness of concrete as required preventing flotation.

          - Grade Rings:  Reinforced-concrete rings shall have minimum wall thickness of one twelfth of the internal diameter, or 4 in., whichever is greater.  Grade rings shall match diameter and thickness of manhole conical riser.  Ring height shall be as required to adjust manhole frame and cover to indicated elevation and slope.

          - Steps:  Individual FRP steps; FRP ladder; or ASTM A615/A 615M, deformed, ½ in. (13 mm) steel reinforcing rods encased in ASTM D4101, PP, wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step.  Cast or anchor steps into sidewalls at 16 in. (400 mm) intervals.  Omit steps if total depth from floor of manhole to finished grade is less than 42 in. (1050 mm).

        - Corrugated Aluminized Steel Detention Systems:

          - Piping shall comply with AASHTO M36 for diameters 12”-144”

          - The material shall be Aluminized Steel Type 2 conforming to AASHTO M274

          - All fittings shall be reinforced per ASTM A998

        - Precast Concrete Three Sided Detention Systems:

          - Precast Concrete Detention Structures shall be manufactured per ASTM C1504

          - Concrete shall be 4000 psi mix and reinforcing steel shall have a minimum yield strength of 600 ksi

        - Manhole Frames and Covers:  ASTM A536, Grade 60-40-18, ductile-iron castings designed for heavy-duty service.  Include 24 in. (610 mm) ID by 7 to 9 in. (175 to 225 mm) riser with 4 in. (102 mm) minimum width flange, and 26 in. (660 mm) diameter cover.  Include indented top design with lettering cast into cover, using wording equivalent to "STORM SEWER."

        - Precast Reinforced Concrete Monolithic Box Sections for Detention Systems:

          - Provide precast box culvert sections for detention systems shall comply with ASTM C1433 or ASTM C1577.

          - Joints shall comply with ASTM C990.

          - External joint wrap shall comply with ASTM C877, Type III.

        - Reinforced Concrete Pipe Detention Systems:

          - Piping shall comply with ASTM C76 for diameters 12”-144”

          - Joints shall comply with ASTM C990 or ASTM C443.

      - PIPE OUTLETS

        - Head Walls:  Construction shall be according to details shown on the drawings.  Headwalls shall be cast-in-place reinforced concrete, with apron and tapered sides unless otherwise indicated.

        - Riprap Aprons:  Broken, irregularly sized and shaped, open graded stone according to Department of Transportation specifications for the state in which the project is located or by using NSSGA's "Quarried Stone for Erosion and Sediment Control”. Unless otherwise shown on the drawings the median stone size used shall be 6 in. (150 mm). Riprap apron will be constructed of stone shaped according to the detail on the Drawings with an underlayment of medium weight non-woven geotextile fabric.

          - Average Size:  NSSGA No. R-6, screen opening 6 in. (150 mm).

        - Concrete Lined Channels:  Construction shall be in accordance with details shown on the drawings.

        - Flared-End Sections: Shall meet Department of Transportation standards for the state in which the project is located unless otherwise indicated on the drawings.

      - DRY WELLS

        - Description:  ASTM C913, precast, reinforced, perforated concrete rings.  Include the following:

          - Floor:  Cast-in-place concrete.

          - Cover:  Liftoff-type concrete cover with cast-in lift rings.

          - Wall Thickness:  4 in. (102 mm) minimum with 1 in. (25 mm) diameter or 1 by 3 in. (25 by 76 mm) maximum slotted perforations arranged in rows parallel to axis of ring.

            - Total Free Area of Perforations:  Approximately 15 percent of ring interior surface.

            - Ring Construction:  Designed to be self-aligning.

          - Filtering Material:  ASTM D448, Size No. 24, 3/4- to 2-1/2 in. (19 to 63 mm) washed crushed stone or gravel.

        - Description:  Manufactured PE side panels and top cover that assemble into 50-gal. (190-L) storage capacity units.

          - Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on Drawings.

          - Side Panels:  With knockout ports for piping and seepage holes.

          - Top Cover:  With knockout port for drain.

          - Filter Fabric:  As recommended by unit manufacturer.

          - Filtering Material:  ASTM D448, Size No. 24, 3/4- to 2-1/2 in. (19 to 63 mm) washed crushed stone or gravel.

        - Description:  Constructed-in-place aggregate type.  Include the following:

          - Lining:  Concrete blocks or precast concrete rings with notches or weep holes.

          - Filtering Material:  ASTM D448, Size No. 24, 3/4- to 2-1/2 in. (19- to 63 mm) washed crushed stone or gravel.

          - Cover:  Precast, reinforced-concrete slab designed for structural loading according to ASTM C890 and made according to ASTM C913.  Include slab dimensions that will extend 12 in. (300 mm) minimum beyond edge of excavation, with bituminous coating over entire surface.  Cast cover with opening for manhole in center.

          - Manhole:  24 in. (610-mm) diameter, reinforced concrete access lid with steel lift rings.  Include bituminous coating over entire surface.

      - STORMWATER DISPOSAL SYSTEMS

        - Chamber Systems:

          - Chambers shall meet the requirements of ASTM F2418 and meet the safety factors recommended by Section 12.12 of the AASHTO LRFD Bridge Design Specifications. Loads for design shall be calculated in accordance with Section 3 of the AASHTO LRFD Bridge Design Specifications.

          - The chamber manufacturer shall provide design data in accordance with ASTM F2418. Installation shall be in accordance with the details shown on the Drawings.

          - Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on Drawings  or comparable product by one of the following:

            - Advanced Drainage Systems. 4640 Trueman Blvd., Hilliard, Ohio 43026 (800) 821-6710

            - CULTEC, Inc. 878 Federal Road, PO Box 280, Brookfield, CT 06804 (800) 4-CULTEC.

            - Hancor Inc. 401 Olive Street, Findlay, OH 45840 (888) FOR-PIPE.

            - StormTech LLC. 20 Beaver Road, Wetheresfield , CT 06109 (888) 892-2694

          - Storage and Leaching Chambers:  Chamber rows shall provide continuous, unobstructed internal space with no internal support panels in order to provide ease of access for inspection and maintenance. Include number of chambers, distribution piping, end plates, and other standard components as required for system total capacity.

          - Geotextile: Shall be enclosed in geotextile fabric for sediment capture and maintenance. Fabric shall be located per manufacturer’s details.

            - Geotextile woven or spun filter fabric, in one or more layers, for minimum total unit weight of 4 oz./sq. yd. (135 g/sq. m).

            - Fabric between chamber bottom and the stone foundation shall be AASHTO M288 Class 1 woven for stabilization and filtration.

            - Fabric between the top of the chamber and the embedment stone shall be AASHTO M288 Class 2 non-woven for separation.

          - Filtering Material:  ASTM D 448, Size No. 24, 3/4- to 2-1/2 in. (19 to 63 mm) washed, crushed stone or gravel.

        - Pipe Systems:

          - Perforated manifold lateral piping complying with AASHTO M 252 or AASHTO M 294, including fittings, couplings, seals, and filter fabric.

          - Fully perforated Aluminized Steel Type 2 Recharge/Detention System conforming to AASHTO M36. All fittings to be reinforced per ASTM A998.

          - Basis of Design Product:  Subject to compliance with requirements, provide product indicated on Drawings or comparable product by one of the following:

            - Advanced Drainage Systems. 4640 Trueman Blvd., Hilliard, Ohio 43026 (800) 433-7473

            - Hancor Inc. 401 Olive Street, Findlay, OH 45840 (800) 848-3546.

            - CONTECH Construction Products, Inc. 9025 Centre Pointe Drive, West Chester, Ohio 45069 (336) 854-2177

            - Lane Enterprises, Inc., 3905 Hartzdale Drive Suite 514, Camp Hill, PA 17011 (717) 761-8175.

- EXECUTION

      - EARTHWORK

        - Excavation, trenching, and backfilling are specified in Division 2 “Earthwork”.

      - PIPING INSTALLATION

        - Locations and Arrangements:  Contractor shall install all drainage structures, pipe, and chambers in the locations shown on the drawings and/or as approved by the Owner. Pipe shall be of the type and sizes specified on the drawings and shall be laid accurately to line and grade. Structures shall be accurately located and properly oriented. Where specific installation is not indicated, follow piping manufacturer's written instructions.

        - Install piping beginning at low point, on prepared foundation, true to grades and alignment indicated with unbroken continuity of invert.  Place bell ends of piping facing upstream.  Install gaskets, seals, sleeves, and couplings according to manufacturer's written instructions for use of lubricants, cements, and other installation requirements. Lap joint pipes shall be laid with the inside circumferential laps pointing downstream and with the longitudinal laps at the side or quarter points.

        - Install chambers in accordance with manufacturer’s guidelines. Rows of chambers shall be laid out using spacers or appropriate measurements and markings to ensure proper spacing between rows for proper backfill and compaction as specified by the manufacturer.

        - Manholes, catch basins, and drain inlets shall be constructed as soon as the pipe laying reaches the location of the structures. If the Contractor continues pipe installation without making provisions for completion of the structures, the Owner shall have the authority to stop the pipe installation until the structure is completed.

        - Any structure which is miss-located or oriented improperly shall be removed and reconstructed at its proper location, alignment, and orientation without cost to the Owner.

        - Install manholes for changes in direction unless fittings are indicated.  Use fittings for branch connections unless direct tap into existing storm drainage is indicated.

        - Precast drainage structures shall be assembled in accordance with the manufacturer’s instructions to form a sound structural unit.

        - Cast-in-Place drainage structures shall be installed in accordance with the details or referenced specifications shown on the drawings. Concrete shall comply with the requirements of this section.

        - Solid concrete brick masonry structures shall be installed in accordance with the details or referenced specifications shown on the drawings. Only solid masonry units may be used. Minimum wall thickness shall be 8 in. and minimum bottom slab thickness shall be 6 in. and extended a minimum of 6 in. outside the structure.

        - Fittings and Connections:

          - Silt-Tight Connections:  Reinforced concrete pipe connections to drainage structures shall be made so that the pipe does not project beyond the inside wall of the drainage structure and shall be grouted only with Non-Shrink Grout (ASTM C1107) per detail to make smooth and uniform surfaces on the inside of the structure. Connection material shall not include large stone, broken block or other deleterious material.

          - Leak-Resistant Connections:  Provide a flexible, leak-resistant boot connection to drainage structures for ALL flexible pipe materials (PVC, HDPE, CMP, DIP, etc.).  For HDPE pipe, provide a flexible boot connection in accordance with ASTM F2510.  Where designated on the drawings, provide a boot connection for reinforced concrete pipe meeting ASTM C923.  Bottom invert connections shall be constructed of concrete form smooth to provide a bench between pipe inverts unless otherwise detailed on the plans.

        - Install proper size increasers, reducers, and couplings where different sizes or materials of pipes and fittings are connected.  Reducing size of piping in direction of flow is prohibited.

        - When installing pipe under streets or other obstructions that cannot be disturbed, use pipe-jacking process of micro-tunneling.

        - Install gravity-flow, non-pressure drainage piping according to the following:

          - Install piping pitched down in direction of flow.

          - Install piping NPS 6 (DN 150) and larger with restrained joints at tee fittings and at changes in direction.  Use corrosion-resistant rods, pipe, or fitting manufacturer's proprietary restraint system, or cast-in-place concrete supports or anchors.

          - Install piping with 24 in. (610 mm) minimum cover.

          - Install hub-and-spigot, cast-iron soil piping according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook."

          - Install hubless cast-iron soil piping according to CISPI 310 and CISPI's "Cast Iron Soil Pipe and Fittings Handbook."

          - Install ductile-iron piping and special fittings according to AWWA C600 or AWWA M41.

          - Install corrugated steel piping according to ASTM A798 and/or Section 26 of the AASHTO LRFD Bridge Construction Specifications.

          - Install HDPE piping according to ASTM D2321 and/or Section 30 of the AASHTO LRFD Bridge Construction Specifications..

          - Install PVC profile gravity sewer piping according to ASTM D2321 and ASTM F1668.

          - Install reinforced-concrete sewer piping according to ASTM C1479 and ACPA's "Concrete Pipe Installation Manual."

        - Install corrosion-protection piping encasement over the following underground metal piping according to ASTM A674 or AWWA C105:

          - Hub-and-spigot, cast-iron soil pipe and fittings.

          - Hubless cast-iron soil pipe and fittings.

          - Ductile-iron pipe and fittings.

          - Expansion joints and deflection fittings.

      - PIPE JOINT CONSTRUCTION

        - Join gravity-flow, nonpressure drainage piping according to the following:

          - Join hub-and-spigot, cast-iron soil piping with gasketed joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for compression joints.

          - Join hub-and-spigot, cast-iron soil piping with calked joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for lead and oakum calked joints.

          - Join hubless cast-iron soil piping according to CISPI 310 and CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for hubless-coupling joints.

          - Join ductile-iron culvert piping according to AWWA C600 for push-on joints.

          - Join ductile-iron piping and special fittings according to AWWA C600 or AWWA M41.

          - Join corrugated steel sewer piping according to ASTM A798/A798M.

          - Join HDPE pipe according to ASTM D2321

          - Join PVC cellular-core piping according to ASTM D2321 and ASTM F891 for solvent-cemented joints.

          - Join PVC corrugated sewer piping according to ASTM D2321 for elastomeric-seal joints.

          - Join PVC sewer piping according to ASTM D2321 and ASTM D3034 for elastomeric-seal joints or ASTM D3034 for elastomeric-gasketed joints.

          - Join PVC profile gravity sewer piping according to ASTM D2321 for elastomeric-seal joints or ASTM F794 for gasketed joints.

          - Join reinforced-concrete sewer piping according to ACPA's "Concrete Pipe Installation Manual" for rubber-gasketed joints for leak-resistant systems or butyl rubber sealant materials for soil tight systems.

          - Join dissimilar pipe materials with nonpressure-type flexible couplings.

      - BACKWATER VALVE INSTALLATION

        - Install horizontal-type backwater valves in piping where indicated.

        - Install combination horizontal and manual gate-valve type in piping and in manholes where indicated.

        - Install terminal-type backwater valves on end of piping and in manholes where indicated.

      - CLEANOUT INSTALLATION

        - Install cleanouts and riser extensions from sewer pipes to cleanouts at grade.  Use cast-iron soil pipe fittings in sewer pipes at branches for cleanouts and cast-iron soil pipe for riser extensions to cleanouts.  Install piping so cleanouts open in direction of flow in sewer pipe.

          - Use Heavy-Duty, top-loading classification cleanouts in vehicle-traffic service areas.

        - Set cleanout frames and covers in cast-in-place concrete, 24 by 24 by 6 in. (600 by 600 by 150 mm) deep.  Set with tops flush with adjacent grade. At pavement areas and at roads set frames and covers with tops flush pavement surface.

      - DRAIN INSTALLATION

        - Install type of drains in locations indicated.

          - Use Heavy-Duty, top-loading classification drains in vehicle service areas.

        - Install drains according to details on the plans and manufacturer’s installation requirements..

        - Fasten grates to drains if indicated.

        - Set drain frames and covers with tops flush with pavement surface.

        - Assemble trench sections with flanged joints.

      - MANHOLE INSTALLATION

        - General:  Install manholes, complete with appurtenances and accessories indicated.

        - Install precast concrete manhole sections with sealants according to ASTM C891.

        - Where specific manhole construction is not indicated, follow manhole manufacturer's written instructions.

        - Set tops of frames and covers flush with finished surface of manholes that occur in pavements.  Set tops 3 in. (76 mm) above finished surface elsewhere unless otherwise indicated.

      - CATCH BASIN INSTALLATION

        - Construct catch basins to sizes and shapes indicated.

        - Frames, Grates and Hoods

          - Set frames and grates to elevations indicated.

          - Firmly embedded in mortar approximately 1 in. thick and aligned to fit the top section of the structure.

          - Brick set in mortar used to adjust the frame to finished grade shall be limited to no more than four (4) courses for precast structures and have a minimum wall thickness of 8 in.

      - STORMWATER INLET AND OUTLET INSTALLATION

        - Construct inlet head walls, aprons, and sides of reinforced concrete, as indicated.

        - Construct riprap of broken stone, as indicated.

        - Install outlets that spill onto grade, anchored with concrete, where indicated.

        - Install outlets that spill onto grade, with flared end sections that match pipe, where indicated.

        - Construct energy dissipaters at outlets, as indicated.

      - MODIFICATION OF EXISTING STRUCTURES

        - General: The Contractor shall alter, reconstruct and/or convert existing structures where and as shown on the drawings, and/or as approved by the Owner. Alterations shall be performed with the same type, grade and quality material as used in the original construction unless otherwise indicated on the drawings or approved by the Owner.

        - Damage to Existing Structures: The Contractor shall exercise care during all alterations, reconstructions, or conversions so as not to damage any portion of the existing structures or pipe to remain. Any damage caused by the Contractor shall be repaired by the Contractor at its own expense and to the satisfaction to the Owner.

      - ROOF DRAINS AND LEADERS

        - The site Contractor shall install roof downspout leaders as shown on the drawings to within 5 ft. of the building limits. If work by others is complete then the Contractor shall complete the connection. If future connections will be required by others, the Contractor shall install plugging and material apparatus as necessary to protect and mark the location of its work.

        - All roof drain leader piping connections shall utilize watertight prefabricated fittings and drainage structures.

      - DRY WELL INSTALLATION

        - Excavate hole to diameter of at least 6 in. (150 mm) greater than outside of dry well.  Do not extend excavation into ground-water table.

        - Install precast, concrete-ring dry wells according to the following:

          - Assemble rings to depth indicated.

          - Extend rings to height where top of cover will be approximately 8 in. (203 mm) below finished grade.

          - Backfill bottom of inside of rings with filtering material to level at least 12 in. (300 mm) above bottom.

          - Extend effluent inlet pipe 12 in. (300 mm) into rings and terminate into side of tee fitting.

          - Backfill around outside of rings with filtering material to top level of rings.

          - Install cover over top of rings.

        - Install manufactured, PE dry wells according to manufacturer's written instructions and the following:

          - Assemble and install panels and cover.

          - Backfill bottom of inside of unit with filtering material to level at least 12 in. (300 mm) above bottom.

          - Extend effluent inlet pipe 12 in. (300 mm) into unit and terminate into side of tee fitting.

          - Install filter fabric around outside of unit.

          - Install filtering material around outside of unit.

        - Install constructed-in-place dry wells according to the following:

          - Install brick lining material dry and laid flat, with staggered joints for seepage.  Build to diameter and depth indicated.

          - Install block lining material dry, with staggered joints and 20 percent minimum of blocks on side for seepage.  Install precast concrete rings with notches or weep holes for seepage.  Build to diameter and depth indicated.

          - Extend lining material to height where top of manhole will be approximately 8 in. (203 mm) below finished grade.

          - Backfill bottom of inside of lining with filtering material to level at least 12 in. (300 mm) above bottom.

          - Extend effluent inlet pipe 12 in. (300 mm) into lining and terminate into side of tee fitting.

          - Backfill around outside of lining with filtering material to top level of lining.

          - Install manhole over top of dry well.  Support cover on undisturbed soil.  Do not support cover on lining.

      - CONCRETE PLACEMENT

        - Place cast-in-place concrete according to ACI 318 and ACI 350R.

        - No concrete or masonry shall be placed when the temperature is below 40 degrees Fahrenheit, or when indications are for lower temperatures within 24 hours, unless protection of concrete and masonry is approved by the Owner. Damage to the structure because of freezing shall be corrected by the Contractor at the Contractor’s sole expense and to the satisfaction of the Owner.

      - STORMWATER DISPOSAL SYSTEM INSTALLATION

        - Chamber Systems:  Excavate trenches of width and depth, and install system and backfill according to chamber manufacturer's written instructions.  Include storage and leaching chambers, filtering material, and filter mat.

        - Piping Systems:  Excavate trenches of width and depth, and install piping system, filter fabric, and backfill, according to piping manufacturer's written instructions.

      - CONNECTIONS

        - Connect nonpressure, gravity-flow drainage piping in building's storm building drains as specified in Division 15 Section “Basic Mechanical Materials and Methods”.

        - Connect force-main piping to building's storm drainage force mains specified in Division 15 Section “Basic Mechanical Materials and Methods”. Terminate piping where indicated.

        - Compliance with Existing Facilities:

          - Connections made into existing drainage facilities shall be performed in accordance with the requirements of the Owner of the facility.  Construction within a public right-of-way will conform to all requirements of the regulatory authority having jurisdiction.  The Contractor will be required to comply with all such requirements, including securing all required permits and paying all associated costs related to securing the permits.  Costs associated with connections shall be included in the Contract Sum.

          - The contractor shall make all required connections of the proposed drainage facilities into existing drainage facilities where shown on the drawings and/or as approved by the Owner.

        - Make connections to existing piping and underground manholes.

          - Use commercially manufactured wye fittings for piping branch connections.  Remove section of existing pipe; install wye fitting into existing piping; and encase entire wye fitting, plus 6 in. (150-mm) overlap, with not less than 6 in. (150 mm) of concrete with 28-day compressive strength of 3000 psi (20.7 MPa).

          - Make branch connections from side into existing piping, NPS 4 to NPS 20 (DN 100 to DN 500).  Remove section of existing pipe, install wye fitting into existing piping, and encase entire wye with not less than 6 in. (150 mm) of concrete with 28-day compressive strength of 3000 psi (20.7 MPa).

          - Make branch connections from side into existing piping, NPS 21 (DN 525) or larger, or to underground manholes and structures by cutting into existing unit and creating an opening large enough to allow 3 in. (76 mm) of concrete to be packed around entering connection.  Cut end of connection pipe passing through pipe or structure wall to conform to shape of and be flush with inside wall unless otherwise indicated.  On outside of pipe, manhole, or structure wall, encase entering connection in 6 in. (150 mm) of concrete for minimum length of 12 in. (300 mm) to provide additional support of collar from connection to undisturbed ground.

            - Use concrete that will attain a minimum 28-day compressive strength of 3000 psi (20.7 MPa) unless otherwise indicated.

            - Use epoxy-bonding compound as interface between new and existing concrete and piping materials.

          - Protect existing piping, manholes, and structures to prevent concrete or debris from entering while making tap connections.  Remove debris or other extraneous material that may accumulate.

        - Connect to sediment interceptors specified in Section "Sanitary Sewer."

        - Pipe couplings, expansion joints, and deflection fittings with pressure ratings at least equal to piping rating may be used in applications below unless otherwise indicated.

          - Use nonpressure-type flexible couplings where required to join gravity-flow, nonpressure sewer piping unless otherwise indicated.

            - Shielded flexible couplings for same or minor difference OD pipes.

            - Unshielded, increaser/reducer-pattern, flexible couplings for pipes with different OD.

            - Ring-type flexible couplings for piping of different sizes where annular space between smaller piping's OD and larger piping's ID permits installation.

          - Use pressure-type pipe couplings for force-main joints.

      - CLOSING ABANDONED STORM DRAINAGE SYSTEMS

        - Abandoned Piping:  Close open ends of abandoned underground piping indicated to remain in place.  Include closures strong enough to withstand hydrostatic and earth pressures that may result after ends of abandoned piping have been closed.  Use either procedure below:

          - Close open ends of piping with at least 8 in.  (203 mm) thick, brick masonry bulkheads.

          - Close open ends of piping with threaded metal caps, plastic plugs, or other acceptable methods suitable for size and type of material being closed.  Do not use wood plugs.

        - Abandoned Manholes and Structures:  Excavate around manholes and structures as required and use one procedure below:

          - Remove manhole or structure and close open ends of remaining piping.

          - Remove and backfill manhole locations as recommended in the geotechnical report and as indicated on the Drawings.

          - If not indicated in the geotechnical report or on the Drawings, remove top of manhole or structure down to at least 36 in. (915 mm) below final grade.  Fill to within 12 in. (300 mm) of top with stone, rubble, or gravel.  Fill to top with concrete.

        - Backfill to grade according to Division 2 Section "Earth Work."

      - IDENTIFICATION

        - Materials and their installation are specified in Division 2 Section "Earth Work." Arrange for installation of green warning tape directly over piping and at outside edge of underground structures.

          - Use detectable warning tape over all storm drainage piping and over edges of underground structures.

      - PROTECTION AND CLEANING

        - The Contractor shall maintain all pipe and chamber installations and drainage structures in a condition such that they will function continuously and shall be kept clean of silt, debris, and other deleterious substances until the project has achieved final acceptance.

        - The Contractor shall use all erosion and sediment control measures necessary to assure construction sediments (or other pollutants) do not reach stormwater pipe and/or chamber installations.

      - FIELD QUALITY CONTROL

        - Inspect interior of piping to determine whether line displacement or other damage has occurred.  Inspect after approximately 24 in. (610 mm) of backfill is in place, and again at completion of Project (See 3.20 Post Installation Inspection).

          - Submit separate signed reports for each system inspection.

          - Defects requiring correction include the following:

            - Alignment:  Less than full diameter of inside of pipe is visible between structures.

            - Deflection:  Flexible piping with deflection exceeding 5%.

            - Damage:  Crushed, broken, cracked, or otherwise damaged piping.

            - Infiltration or Ex-filtration: Water leakage into or out of the installed piping when leak-resistant connections are provided.  Maximum infiltration or ex-filtration rate of 250 gals./in.dia./mile of piping/24 hours.

          - Replace defective piping using new materials, and repeat inspections until defects are within allowances specified.

          - Re-inspect and repeat procedure until results are satisfactory.

        - Test new piping systems, and parts of existing systems that have been altered, extended, or repaired, for leaks and defects.

          - Do not enclose, cover, or put into service before inspection and approval.

          - Test completed piping systems according to requirements in Section 3.20.

          - Schedule tests and inspections by authorities having jurisdiction with at least 24 hours advance notice.

          - Submit separate report for each test.

          - Gravity Flow Storm Drainage Piping:  Test according to requirements of authorities having jurisdiction, UNI-B-6, and the following:

            - Exception:  Piping with soil tight joints unless required by authorities having jurisdiction.

            - Option:  Test plastic piping according to ASTM F1417.

            - Option:  Test concrete piping according to ASTM C924, ASTM C969 or ASTM C1103.  Note, pipe tested in accordance with ASTM C924 or ASTM C969 shall be filled with water and allowed to saturate for 72 hours prior to conducting field tests.

          - Force Main Storm Drainage Piping:  Perform hydrostatic test after thrust blocks, supports, and anchors have hardened.  Test at pressure not less than 1-1/2 times the maximum system operating pressure, but not less than 150 psig (1035 kPa).

            - Ductile-Iron Piping:  Test according to AWWA C600, "Hydraulic Testing" Section.

            - PVC Piping:  Test according to AWWA M23, "Testing and Maintenance" Chapter.

        - Leaks and loss in test pressure constitute defects that must be repaired.

        - Repair or replace leaking piping using new materials, and repeat testing until leakage is within allowances specified.

      - POST INSTALLATION INSPECTIONS

        - Upon completion of the work and before final acceptance by the Owner, the entire drainage system shall be subject to a final inspection in the presence of the Owner and/or the Project Engineer.  The work shall not be considered complete until all requirements for line, grade, cleanliness, workmanship, and final inspections have been completed.  Final inspection of the completed pipe installations will be performed after the embankment and/or trench fill is in place and all non-asphalt bases and/or sub-grades have been completed for at least 30 days.

        - Second Final Post Installation Inspection: (If required for the Project) The Owner shall require a second final post installation inspection.

          - Final post installation inspections (if required) shall be conducted no sooner than 2 months before the end of the one year warranty.

          - Final post installation inspections shall utilize a video camera and laser profiler/deflectometer or a video camera and go-no-go Mandrel.  Lasers shall be calibrated to the pipe diameter as shown on the construction plans.

        - Initial and final post installation inspections shall be performed and reported, at the Contractor’s expense, by a National Association of Sewer Service Companies (NASSCO) Certified Pipe Inspector. Reports of storm pipe assessments shall be submitted to the Project Engineer for review and appraisal.

        - The initial and post installation inspection report shall include: a copy of all video taken (if required), pipe location identification, equipment used for inspection, inspector name, deviation from design grade, deviation from line, deflection of pipe system, inspector notes, condition of joints, condition of pipe wall (e.g. Distress, cracking, wall damage dents, bulges, creases, tears, holes, etc…), ovality and flow capacity.

        - For RCP: Initial and post installation inspections shall be subject to the limits defined in Section 27 of the AASHTO LRFD Bridge Construction Specifications.  Cracks having a width greater 0.05 to 0.10 inches shall be evaluated based on the site’s environmental conditions.  Pipe’s having cracks greater than 0.10 inch shall be evaluated and remediated.

        - For CMP and HDPE: initial and post installation inspection deflections shall be subject to the limits defined in Section 26 (Metal Culverts) and Section 30 (Thermoplastic Pipe) of the AASHTO LRFD Bridge Construction Specifications.  The initial post installation deflection shall not exceed 5% and the final post installation deflection shall not exceed 7% deflection.

      - CLEANING

        - Clean interior of piping of dirt and superfluous materials. Flush with water.

END OF SECTION 02630

CONFORMANCE SUBMITTAL

# SECTION 02630 – STORM UTILITY DRAINAGE PIPING

Lowe’s of                   ________________________________________________________________                                                                                    					(City, State)

General Contractor:	________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

Sub-Contractor:		________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

The following products have been selected (check one box) for use in this project from the list of acceptable products specified:

Concrete Pipe, ASTM C76, Butyl mastic joint sealant ASTM C990 for silt-tight designations or rubber gaskets meeting the material and joint configuration requirements of ASTM C443 for leak-resistant designations:

Tongue and Groove RCP, with ASTM C990 preformed flexible sealant, ASTM C76 Class _____

Bell and Spigot RCP, with ASTM C443 rubber gasket, ASTM C76 Class _____

Manufacturer: _________________________________________________________________

Is the concrete pipe manufacturer a member of the American Concrete Pipe Association?         Yes        No

(A listing of ACPA member can be found at: http://www.concrete-pipe.org/pages/locator.html)

Precast Reinforced Concrete Monolithic Box Sections, ASTM C1433 or ASTM C1577:

RCB conforms to ASTM C1433.

RCB conforms to ASTM C1577.

Tongue and Groove joint with ASTM C990 preformed flexible sealant.

Design Fill Height = __________ feet.

Design Live Load = _____________________________________________________.

Manufacturer: ___________________________________________________________

Is the concrete pipe manufacturer a member of the American Concrete Pipe Association?         Yes        No

(A listing of ACPA member can be found at: http://www.concrete-pipe.org/pages/locator.html)

Precast Reinforced Concrete Elliptical Pipe, ASTM C507:

REP conforms to ASTM C507 Class ___________.

Tongue and Groove REP, with ASTM C990 preformed flexible sealant.

Manufacturer: ___________________________________________________________

Is the concrete pipe manufacturer a member of the American Concrete Pipe Association?         Yes        No

(A listing of ACPA member can be found at: http://www.concrete-pipe.org/pages/locator.html)

# High Density Polyethylene (HDPE) Pipe, AASHTO M252, M294, Rubber Gasket Joints ASTM F477, silt-tight or watertight designations as specified:

ADS Pipe

Hancor Pipe

Lane Pipe

Quality Culvert Pipe

DuroMaxx

All underground connections will be made with pre-fabricated HDPE fittings

# Polyvinyl Chloride (PVC) Pipe, Rubber Gasket Joints ASTM F477:

PVC Pipe, ASTM D3034, SDR 35

Corrugated PVC Pipe, Contech “A2000”

All underground connections will be made with pre-fabricated PVC fittings

# Aluminized Steel Type 2 Corrugated Steel Pipe (CMP), AASHTO M36/M274 or ASTM A760/A929, silt-tight or watertight designations as specified:

Aluminized Steel Type2 Corrugated Steel Pipe

# Aluminized Steel Type 2 Spiral Ribbed Pipe (Type IR), AASHTO M274 or ASTM A929 and AASHTO M36 or ASTM A760, silt-tight or watertight designations as specified:

Aluminized Steel Type 2 Spiral Ribbed Pipe (Type IR)

# Ductile Iron Pipe (DIP), AWWA C151, Fittings AWWA C110, Gaskets AWWA C111:

DIP

# Stormwater Collection Chambers ASTM F2418

StormTech

Hancor

CULTEC

StormTech by ADS

Stormwater Detention or Recharge System

Aluminized Steel CMP Detention 	Fully Perforated CMP Detention/Recharge 	Precast Concrete Detention System

Drainage Boxes (Must be pre-cast unless approved by Lowe’s):

Pre-cast Concrete, per specifications by: Lowe’s, DOT #_______, City #_______, Other _______

Cast-in-place Concrete, per specifications by: Lowe’s, DOT #_____, City #______, Other________

Solid Concrete Brick Masonry, per specifications by: Lowe’s, DOT # ___________,

City #__________, Other _______________

Cast Iron Frames, Grates, and Hoods:

Manhole lids, per specifications by: Lowe’s, DOT #________, City #________, Other_____

Curb Inlets, per specifications by: Lowe’s, DOT #________, City #________, Other______

Drop Inlets, per specifications by: Lowe’s, DOT #________, City #________, Other______

Detention Pond As-built Survey:

I recognize that an as-built survey of all detention ponds and structures shall be completed prior to project acceptance in accordance with Section 017300 – Field Engineering and Surveying

I represent to Lowe’s that the products selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the contract documents. If noncompliance is discovered the General Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and specifications.  Immediately or as directed by Lowe’s the work shall be completed without additional cost to the Lowe’s and / or the contract.

Sub-Contractor:		________________________________________________________________

(Signature of the Authorized Agent of the Sub-Contractor)				Date

________________________________________________________________

(Print Name of the Authorized Agent of the Sub-Contractor)

General Contractor:	________________________________________________________________

(Signature of the Authorized Agent of the General Contractor)			Date

________________________________________________________________

(Print Name of the Authorized Agent of the General Contractor)

# TRENCH DRAIN CONFORMANCE SUBMITTAL

# SECTION 02630 (Forthcoming Section 334100) – STORM UTILITY DRAINAGE PIPING

Lowe’s of _______________________________________________________________________

(City, State)

General Contractor:	________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

Sub-Contractor:		________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

# Product Verification:

# The trench drains installed in this store will meet the product guidelines of Section 334100-2.13 “POLYMER-CONCRETE, CHANNEL DRAINAGE SYSTEMS”

Truck Well Trench Drain Manufacturer & Model Number:

Grate Model Number:

Seasonal Display Trench Drain Manufacturer & Model Number:

Grate Model Number:

General Contractor’s Affidavit:

I represent to Lowe’s that the product selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the project specification.  If noncompliance is discovered the General Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and Lowe’s specifications.  The work shall be completed immediately as directed by Lowe’s without additional cost to Lowe’s and/or the contract.

General Contractor:	________________________________________________________________

(Signature of the Authorized Agent of the General Contractor)			(Date)

________________________________________________________________

(Print Name of the Authorized Agent of the General Contractor)

Sub-Contractor’s Affidavit:

I represent to Lowe’s that the product selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the project specification.  If noncompliance is discovered the Sub-Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and Lowe’s specifications.  The work shall be completed immediately as directed by Lowe’s and/or the General Contractor without additional cost to Lowe’s and/or the contract.

Sub-Contractor:		________________________________________________________________

(Signature of the Authorized Agent of the Sub-Contractor)				(Date)

________________________________________________________________					 (Print Name of the Authorized Agent of the Sub-Contractor)