SECTION 08363 - SECTIONAL OVERHEAD DOORS (FULL VIEW) (If Indicated On Drawings)

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specifications, apply to this Section.

SUMMARY

This Section includes steel sectional overhead doors (if indicated on the drawings).

See Division 8 Section "Door Hardware" for lock cylinders and keying.

Division 16 Sections for electrical service, connections, disconnects, and circuit breakers for powered operators, and accessories.

PERFORMANCE REQUIREMENTS

Structural Performance:  Provide doors capable of withstanding the effects of gravity loads and the following loads and stresses without evidencing permanent deformation of components:

Wind Load:  per DASMA 102-2003 or to meet local area wind load requirements (whatever is greater).

Operational Life:  Design components to operate for not less than 50,000 cycles for Motorized doors and 10,000 cycles for Manual doors.

Operation Cycle:  One complete cycle begins with door in closed position.  Door is then moved to open position and back to closed position.

Operator:

Hoist commercial operator – 208/230v, 60hz, 3-phase with Miller electric sensing edge

SUBMITTALS

Product Data:  For each product indicated.

Shop Drawings:  Include plans, elevations, sections, details of installation, wiring diagrams, and attachments to other work.  Use same reference designations indicated on Drawings and Door Schedule. Upload information to Site|Folio. (www.sitefolio.net)

Verify openings by field measurements before fabrication and indicate measurements on Shop Drawings.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories (if indicated): Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

PRODUCTS

MANUFACTURERS

For Lowe’s National Account pricing, General Contractor contact:

Julie Perez 1-800-598-3667, Fax 330-763-8038  jperez@wayne-dalton.com

Manufacturers of Power Operated, Aluminum Full View Sectional Door:  Subject to compliance with requirements, as specified, provide products by:

Wayne Dalton.

Aluminum Full View AFV Model 451

Aluminum Full View AFV Model 452 – Insulated (as required)

MATERIALS

Door Sections: Shall be of aluminum alloy 6063-T6, 1-3/8” thick stiles and rails, joined with self tapping screws.

Rails: Top and bottom rails with 3-1/2” wide, lower intermediate rail 1-3/8”, upper rail 1-5/8”, minimum wall thickness 0.062”.

Stiles: Top, bottom and end stiles are 3-1/2” wide, center stile 3” wide, minimum wall thickness 0.062.

Glazing: 1/8” DSB (Model 451); ½” insulated (Model 452)

Finish: Manufacturer’s Anodized Aluminum

Fabricate sections so finished door assembly is rigid and aligned, with tight hairline joints, and free of warp, twist and deformation

TRACKS, SUPPORTS, AND ACCESSORIES

Tracks:  Galvanized steel track system complying with ASTM A 653/A 653M, G60 (Z180) zinc coating, sized for door size and weight, designed for lift type indicated.

Provide complete track assembly including brackets, bracing, and reinforcement for rigid support of ball-bearing roller guides for required door type and size.

Slope tracks at proper angle from vertical or otherwise design to ensure tight closure at jambs when door unit is closed.

Weld or bolt to track supports.

Provide maximum high lift as clearance allows.

Track design shall be Standard lift . Vertical mounting angles shall be hot dipped galvanized. Track size shall be 3”. Vertical track shall be graduated to provide wedge type weathertight closing with continuous angle mounting for steel jambs, and shall be fully adjustable to seal door jambs. Horizontal track shall be reinforced with continuous angle of adequate length and gauge to minimize deflection.

Provide complete track assembly including brackets, bracing and reinforcement for rigid support of ball-bearing roller guides for required door type and size.

Slope tracks at proper angle from vertical or otherwise design to ensure tight closure at jambs when door unit is closed.

Weld or bolt track supports.

Provide maximum high lift as clearance allows.

Track Reinforcement and Supports:  Galvanized steel and support members, complying with ASTM A 36/A 36M and ASTM A 123.  Secure, reinforce, and support tracks as required for door size and weight to provide strength and rigidity without sag, sway, and vibration during opening and closing of doors.

Support and attach tracks to opening jambs with continuous angle welded to tracks and attached to wall.  Support horizontal (ceiling) tracks with continuous angle welded to track and supported by laterally braced attachments to overhead structural members at curve and end of tracks.

Weatherseals:  Replaceable, adjustable, continuous, compressible weather-stripping gaskets of flexible vinyl, rubber, or neoprene fitted to bottom and at top of overhead door.

Jamb Seals:  Continuous flexible seals at door jambs for weathertight installation.

Doors shall be equipped with vinyl joint seals between sections and vinyl “bulb” shaped astragal provided on the bottom section. Optional top seal and jamb seal available.

Hardware: Hinge and Roller Assembly:

General: Heavy-duty, corrosion resistant hardware, with hot-dipped galvanized, stainless-steel, or other corrosion resistant fasteners to suit door type.

Hinges and brackets shall be made from heavy-duty hot dipped, galvanized steel of not less than 14 gauge thick uncoated steel, at each end stile and at intermediate stile, per manufacturer’s written recommendation.

Attach hinges to door sections through stiles and rails with bolts and lock nuts or lock washers and nuts. Use rivets or self-tapping fasteners where access to nuts is impossible.

Use double-end hinges, where required, for doors exceeding 16 feet (4.87 m) in width, unless otherwise recommended by door manufacturer.

All factory authorized attachments shall be made at locations indicated.

Reinforce for hardware attachment.

Rollers: Heavy-duty long stem rollers, with minimum 10 steel ball bearings in case-hardened steel races, mounted with varying projections to suit slope of track.

Track rollers shall be case-hardened inner steel races with 10-ball, 3” rollers.

Double hinges: Extend roller shaft through hinges.

Roller tire: 3-inch (75 mm) diameter roller tires for 3-inch (75 mm) track.

Tire Material: Case hardened steel.

Slide bolt: Fabricate with side locking bolts to engage through slots in tracks for locking by padlock, located on single-jamb side, operable from inside only.

COUNTERBALANCING MECHANISM

Torsion Spring:  Operation by counterbalance mechanism with adjustable-tension torsion springs, fabricated from oil-tempered-steel wire complying with ASTM A 229/A 229M, Class II, mounted on cross-header  solid steel shaft.  Connect to door with galvanized aircraft-type lift cables with cable safety factor of at least 5 to 1.  Calibrate springs for 50,000 cycles.

Springs shall be torsion type, low-stress, helical wound, oil-tempered spring wire on continuous steel solid shaft.

Cable Drums:  Cast-aluminum or gray-iron castings grooved to receive cable.  Mount counterbalance mechanism with ball-bearing brackets at each end of shaft.

Include one additional midpoint bracket for shafts up to 16 feet (4.87 m) long.

Include two additional brackets at 1/3 points to support shafts more than 16 feet (4.87 m) long, unless closer spacing is recommended by door manufacturer.

Bracket:  Anchor support bracket, as required to connect stationary end of spring to the wall, to level shaft and prevent sag.

Leaf Spring Bumper:  Include at each horizontal track to cushion door at end of opening operation.

WARRANTY

Manufacturer’s standard one year warranty against defects in workmanship and material

OPERATION

Provide hoist type electric operator, to operate the door at an approximate speed of 1’-0” (300mm) per second, and as required for door and lift conditions.

Hoist Commercial Operator:  (220 voltage supply as provided by electrical contractor), complete with solenoid brake. Provide ¾ HP. Provide auxiliary chain hoist disconnect beside each door opening to open door in case of power failure.

One push button station (EEMAC 4), “OPEN/CLOSE/STOP”, complete with keyed lock out, mounted on the inside of the opening.

Provide and install an electric Sensing Edge) at the bottom edge of door to reverse on contact with an object, as supplied by Wayne Dalton.. Pneumatic safety edges will not be not be accepted.

Provide and install Wayne Dalton Broken Cable Safety Device (BCSD) part # 287360.

ALL LINE VOLTAGE POWER, FUSED DISCONNECTS AND INTERCONNECTIONS SHALL BE PROVIDED BY DIVISION 16. CONDUIT AND WIRING TO REMOTE LOCATIONS, AND EMPTY CONDUIT FOR LOW VOLTAGE WIRING BY DIVISION 16. ALL CONTROL LOW VOLTAGE WIRING AND TERMINATIONS AND ALL OTHER FINAL ADJUSTMENTS, SHALL BE PROVIDED BY THIS SECTION.

Power wiring, disconnect, including terminations to operator by Division 16. Conduit and wire to remote locations including all accessories by Division 16. All terminations including remote push button staion and controls shall be by this Section.

EXECUTION

INSTALLATION

General:  Install door, track, and operating equipment complete with necessary hardware, jamb and head mold strips, anchors, inserts, hangers, and equipment supports.

Fasten vertical track assembly to framing at not less than 24 inches (600 mm) o.c.  Hang horizontal track from structural overhead framing with angle or channel hangers welded and bolt fastened in place.  Provide sway bracing, diagonal bracing, and reinforcement as required for rigid installation of track and door-operating equipment.

Touch up welds with Zinc rich paint.

Lubricate bearings and sliding parts; adjust doors to operate easily, free from warp, twist, or distortion and fitting weathertight for entire perimeter.

DEMONSTRATION

Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain doors

END OF SECTION 08363

This Page Left Intentionally Blank