MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 15110 - VALVES

GENERAL

SUMMARY

This Section includes the following general-duty valves:

Adjust list below to suit Project.

Copper-alloy ball valves.

Swing check valves.

Bronze gate valves.

Cast-iron gate valves.

See Division 2 piping Sections for general-duty and specialty valves for site construction piping.

See Division 13 fire-suppression piping and fire pump Sections for fire-protection valves.

See Division 15 piping Sections for specialty valves applicable to those Sections only.

SUBMITTALS

Completed “Conformance Submittal” included with this Section.

PRODUCTS

MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

In other Part 2 articles where subparagraph titles below introduce lists, the following requirements apply for product selection:

Coordinate subparagraphs retained below with subparagraph titles retained in other Part 2 articles.  Refer to Division 1 Section "Product Requirements."

Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the manufacturers specified.

Caution:  Valve categories and types and manufacturer lists in the following articles were obtained from valve manufacturers' catalogs available when this Section was updated.  Other valve categories, types, materials, and features not listed in these articles are available and may be added if required.

VALVES, GENERAL

Refer to Part 3 "Valve Applications" Article for applications of valves.

Bronze Valves:  NPS 2 and Smaller:  Threaded ends, unless otherwise indicated.

Ferrous Valves NPS 2-1/2 and Larger:  Flanged ends, unless otherwise indicated.

Caution:  Edit pressure ratings and insert temperature ratings in valve articles if valves with higher ratings are required.

Valve Pressure and Temperature Ratings:  Not less than indicated and as required for system pressures and temperatures.

Valve Sizes:  Same as upstream pipe, unless otherwise indicated.

Valve Actuators:

Handwheel:  For valves other than quarter-turn types.

Lever Handle:  For quarter-turn valves NPS 6 and smaller, except plug valves.

Extended Valve Stems:  On insulated valves.

Valve Flanges:  ASME B16.1 for cast-iron valves, ASME B16.5 for steel valves, and ASME B16.24 for bronze valves.

Valve Grooved Ends:  AWWA C606.

Although soldered connections are common in smaller sizes of plumbing piping, they are not recommended for valves in HVAC service.  Soldering and brazing methods used to achieve required pressure-temperature ratings may damage internal valve parts.  Special installation requirements for soldered valves may make threaded valves more cost-effective.

Solder Joint:  With sockets according to ASME B16.18.

Caution:  Use solder with melting point below 840 deg F for angle, check, gate, and globe valves; below 421 deg F for ball valves.

Threaded:  With threads according to ASME B1.20.1.

Press Fittings:  Provide to match the Viega ProPress piping system in 15050 2.01 (B) and 3.02 (B).

Valve Bypass and Drain Connections:  MSS SP-45.

COPPER-ALLOY BALL VALVES

Retain "Available" in first paragraph below for nonproprietary and delete "Available" for semiproprietary specifications.

Copper-Alloy Ball Valves, General:  MSS SP-110.

Caution:  Two-piece ball valves with a full or regular port are recommended for most services.  One-piece ball valves are suitable if economy is main consideration.  Three-piece ball valves are recommended if disassembly without removing valve from piping is required.

Add specific materials, attributes, and features to paragraphs below to suit Project.

Two-Piece, Copper-Alloy Ball Valves: Bronze body with  regular-port, chrome-plated bronze ball; PTFE or TFE  seats; and 600-psig  minimum CWP rating and blowout-proof stem.

BRONZE GATE VALVES

Retain "Available" in first paragraph below for nonproprietary and delete "Available" for semiproprietary specifications.

Bronze Gate Valves, General:  MSS SP-80, with ferrous-alloy handwheel color coded for water temperature.

Hot Water:  Red.

Cold Water:  Blue.

Add specific materials, attributes, and features to paragraphs below to suit Project.

Type 1, Class 125, Bronze Gate Valves:  Bronze body with nonrising stem and bronze solid wedge and union-ring bonnet, 200-psi CWP.

EXECUTION

VALVE APPLICATIONS

Delete applications below if they are covered in corresponding piping Sections.

Refer to piping Sections for specific valve applications.  If valve applications are not indicated, use the following:

Shutoff Service:  Ball or gate  valves.

If valves with specified SWP classes or CWP ratings are not available, the same types of valves with higher SWP class or CWP ratings may be substituted.

This Section is arranged to provide copper-alloy valves in NPS 2 (DN 50) and smaller and ferrous-alloy valves in NPS 2-1/2 (DN 65) and larger.  Edit sizes for copper- and ferrous-alloy valves to suit Project.  Many types of copper-alloy valves are made in at least NPS 4 (DN 100).  Many ferrous-alloy valves are made in NPS 2 (DN 50) and larger.

Caution:  Verify that valve classes and pressure and temperature ratings are adequate for system fluid.  Repeat each category listing if necessary and add required pressure range for each listing.  Indicate different pressure systems on Drawings.

Valves in categories below are recommended.  Delete valve types not required and add required types from Part 2 articles.

Delete low-pressure, compressed-air piping applications below if compressed-air valves are covered in Division 15 Section "Compressed-Air Piping."

Domestic Water Piping:  Use the following types of valves:

Ball Valves, NPS 2 and Smaller: Two -piece, 400-psig   CWP rating, copper alloy.

Ball Valves, NPS 2-1/2 and Larger:  Class  150, ferrous alloy.

Gate Valves, NPS 2 and Smaller:  Type  1, Class  125, bronze.

Gate Valves, NPS 2-1/2 and Larger:  Type I, Class  125, , bronze-mounted cast iron.

Select valves, except wafer and flangeless types, with the following end connections:

For Copper Tubing, NPS 2 and Smaller:  Solder-joint, ProPress Viega, or threaded ends.

For Steel Piping, NPS 2 and Smaller:  Threaded ends.

For Steel Piping, NPS 2-1/2 to NPS 4:  Flanged or threaded ends.

VALVE INSTALLATION

Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

Install valves with unions or flanges at each piece of equipment arranged to allow service, maintenance, and equipment removal without system shutdown.

Locate valves for easy access and provide separate support where necessary.

Install valves in horizontal piping with stem at or above center of pipe.

Install valves in position to allow full stem movement.

Install check valves for proper direction of flow and as follows:

Edit check valve installation requirements to suit Project.  Delete check valves not required.

Swing Check Valves:  In horizontal position with hinge pin level.

Dual-Plate Check Valves:  In horizontal or vertical position, between flanges.

Lift Check Valves:  With stem upright and plumb.

JOINT CONSTRUCTION

Refer to Division 15 Section “Basic Mechanical Materials and Methods” for basic piping joint construction.

Soldered Joints:  Use ASTM B 813, water-flushable, lead-free flux; ASTM B 32, lead-free-alloy solder; and ASTM B 828 procedure, unless otherwise indicated.

ADJUSTING

Adjust or replace valve packing after piping systems have been tested and put into service but before final adjusting and balancing.  Replace valves if persistent leaking occurs.

END OF SECTION 15110

# CONFORMANCE SUBMITTAL

# Section 15110 – Valves

Lowe’s of _______________________________________________________________________

(City, State)

General Contractor:	________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

Sub-Contractor:		________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

# Product Verification:

The valves installed in this store will meet the product guidelines of Section 15110 “Valves”

General Contractor’s Affidavit:

I represent to Lowe’s that the product selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the project specification.  If noncompliance is discovered the General Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and Lowe’s specifications.  The work shall be completed immediately as directed by Lowe’s without additional cost to Lowe’s and/or the contract.

General Contractor:	________________________________________________________________

(Signature of the Authorized Agent of the General Contractor)			(Date)

________________________________________________________________

(Print Name of the Authorized Agent of the General Contractor)

Sub-Contractor’s Affidavit:

I represent to Lowe’s that the product selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the project specification.  If noncompliance is discovered the Sub-Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and Lowe’s specifications.  The work shall be completed immediately as directed by Lowe’s and/or the General Contractor without additional cost to Lowe’s and/or the contract.

Sub-Contractor:		________________________________________________________________

(Signature of the Authorized Agent of the Sub-Contractor)				(Date)

________________________________________________________________									(Print Name of the Authorized Agent of the Sub-Contractor)