MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 15160 - STORM DRAINAGE PIPING

GENERAL

SUMMARY

This Section includes storm drainage piping inside the building.

QUALITY ASSURANCE

Piping materials shall bear label, stamp, or other markings of specified testing agency.

Delete below if NSF markings are not required.

Comply with NSF 14, "Plastics Piping Systems Components and Related Materials," for plastic piping components.  Include marking with "NSF-drain" for plastic drain piping and "NSF-sewer" for plastic sewer piping.

PRODUCTS

PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for a discussion of this Section's organization and the most efficient way to edit this Section.

Flexible Transition Couplings for Underground Nonpressure Piping:  ASTM C 1173 with elastomeric sleeve.  Include ends of same sizes as piping to be joined and include corrosion-resistant metal band on each end.

Edit first paragraph below for specific type, grade, or schedule number if required.

PVC Pipe:  ASTM D 2665, solid-wall drain, waste, and vent.

PVC Socket Fittings:  ASTM D 2665, made to ASTM D 3311, drain, waste, and vent patterns.

Cellular-Core, Schedule 40, PVC Pipe:  ASTM F 891, Schedule 40.

PVC Socket Fittings:  ASTM D 2665, made to ASTM D 3311, drain, waste, and vent patterns and to fit Schedule 40 pipe.

Cellular-Core, Sewer and Drain Series, PVC Pipe:  ASTM F 891, Series PS 100.

PVC Socket Fittings:  ASTM D 2665, made to ASTM D 3311, drain, waste, and vent patterns and to fit Series PS 100 sewer and drain pipe.

PVC Special Fittings:  ASTM F 409, drainage-pattern tube and tubular fittings with ends as required for application.

EXECUTION

PIPING APPLICATIONS

Select piping applications from this Article.  Coordinate with materials specified in Part 2.  Edit to suit Project.

Transition and special fittings with pressure ratings at least equal to piping pressure ratings may be used in applications below, unless otherwise indicated.

Flanges may be used on aboveground pressure piping, unless otherwise indicated.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

Aboveground Storm Drainage Piping:  Use the following piping materials for each size range:

Retain one or more of eight subparagraphs and associated subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

NPS 2 to NPS 12:  Cellular-core, Schedule 40, PVC pipe; PVC socket fittings; and solvent-cemented joints.

Retain one or more of eight subparagraphs and associated subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

Underground Storm Drainage Piping:  Use the following piping materials for each size range:

Retain one or more of eight subparagraphs and associated subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

NPS 3 to NPS 12:  Cellular-core, Schedule 40, PVC pipe; PVC socket fittings; and solvent-cemented joints.

Retain one or more of eight subparagraphs and associated subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

PIPING INSTALLATION

Storm sewer piping outside the building is specified in Division 2 Section "Storm Drainage."  Edit first paragraph below to suit Project.

Refer to Division 2 Section 2630 "Storm Drainage" for Project site storm sewer and drainage piping.

Refer to Division 15 Section "Basic Mechanical Materials and Methods" for basic piping installation.

Install cleanouts at grade and extend to where building storm drains connect to building storm sewers.

Install cleanout fitting with closure plug inside the building in storm drainage force-main piping.

Retain one of first two paragraphs below for pipe.  Edit or delete to suit Project.  Edit first paragraph for other sleeve material options.

Make changes in direction for storm piping using appropriate branches, bends, and long-sweep bends.  Do not change direction of flow more than 90 degrees.  Use proper size of standard increasers and reducers if pipes of different sizes are connected.  Reducing size of drainage piping in direction of flow is prohibited.

Lay buried building drain piping beginning at low point of each system.  Install true to grades and alignment indicated, with unbroken continuity of invert.  Place hub ends of piping upstream.  Install required gaskets according to manufacturer's written instructions for use of lubricants, cements, and other installation requirements.  Maintain swab in piping and pull past each joint as completed.

Install storm drainage piping at the following minimum slopes, unless otherwise indicated:

Edit two subparagraphs below as required by authorities having jurisdiction.

Building Storm Drain:  1 percent downward in direction of flow for piping NPS 3 and smaller; 1 percent downward in direction of flow for piping NPS 4 and larger.

Horizontal Storm-Drainage Piping:  2 percent downward in direction of flow.

Edit or delete first paragraph below to suit Project.

Install PVC storm drainage piping according to ASTM D 2665.

Do not enclose, cover, or put piping into operation until it is inspected and approved by authorities having jurisdiction.

JOINT CONSTRUCTION

Refer to Division 15 Section "Basic Mechanical Materials and Methods" for basic piping joint construction.

PVC Nonpressure Piping Joints:  Join piping according to ASTM D 2665.

HANGER AND SUPPORT INSTALLATION

Delete first paragraph below if not required.

Refer to Division 15 Section "Mechanical Vibration and Seismic Controls" for seismic-restraint devices.

Refer to Division 15 Section "Hangers and Supports" for pipe hanger and support devices.  Install the following.

Maximum spans below were taken from MSS SP-69 for water service and from model plumbing codes.  Most restrictive piping and spacing dimensions are shown.

Install hangers for PVC piping with the following maximum horizontal spacing and minimum rod diameters:

NPS 1-1/2 and NPS 2:  48 inches with 3/8-inch rod.

NPS 3:  48 inches with 1/2-inch rod.

NPS 4 and NPS 5:  48 inches with 5/8-inch rod.

NPS 6:  48 inches with 3/4-inch rod.

Install supports for vertical PVC piping every 48 inches.

Support piping and tubing not listed above according to MSS SP-69 and manufacturer's written instructions.

CONNECTIONS

Connect interior storm drainage piping to exterior storm drainage piping.  Use transition fitting to join dissimilar piping materials.

Connect storm drainage piping to roof drains and storm drainage specialties.

FIELD QUALITY CONTROL

Portions of testing and inspecting requirements below are taken from model plumbing codes.  Edit if requirements vary.

During installation, notify authorities having jurisdiction at least 24 hours before inspection must be made.  Perform tests specified below in presence of authorities having jurisdiction.

Roughing-in Inspection:  Arrange for inspection of piping before concealing or closing-in after roughing-in.

Final Inspection:  Arrange for final inspection by authorities having jurisdiction to observe tests specified below and to ensure compliance with requirements.

Reinspection:  If authorities having jurisdiction find that piping will not pass test or inspection, make required corrections and arrange for reinspection.

Test storm drainage piping according to procedures of authorities having jurisdiction.

CLEANING

Clean interior of piping.  Remove dirt and debris as work progresses.

Protect drains during remainder of construction period to avoid clogging with dirt and debris and to prevent damage from traffic and construction work.

Place plugs in ends of uncompleted piping at end of day and when work stops.

END OF SECTION 15160