MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 15815 - METAL DUCTS

GENERAL

SUMMARY

This Section includes rectangular and round metal ducts and plenums for heating, ventilating, and air-conditioning systems.

See Division 15 Section "Duct Accessories" for dampers, sound-control devices, duct-mounted access doors and panels, turning vanes, and flexible ducts.

QUALITY ASSURANCE

Comply with NFPA 90A, "Installation of Air Conditioning and Ventilating Systems," unless otherwise indicated.

Comply with NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems," unless otherwise indicated.

PRODUCTS

METAL DUCT MATERIAL S

Galvanized, Sheet Steel:  Lock-forming quality; ASTM A 653/A 653M, G90 coating designation; mill-phosphatized finish for surfaces of ducts exposed to view.

Reinforcement Shapes and Plates:  Galvanized steel reinforcement where installed on galvanized, sheet metal ducts; compatible materials for aluminum and stainless-steel ducts.

Tie Rods:  Galvanized steel, 1/4-inch minimum diameter for 36-inch length or less; 3/8-inch minimum diameter for lengths longer than 36 inches.

SEALING MATERIALS

Joint and Seam Tape:  2 inches wide; glass-fiber fabric reinforced.

Joint and Seam Sealant:  One-part, nonsag, solvent-release-curing, polymerized butyl sealant, formulated with a minimum of 75 percent solids.

HANGERS AND SUPPORTS

Building Attachments:  Concrete inserts, powder-actuated fasteners, or structural-steel fasteners appropriate for building materials.

Hanger Materials:  Galvanized, sheet steel or round, threaded steel rod.

Duct Attachments:  Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

Trapeze and Riser Supports:  Steel shapes complying with ASTM A 36/A 36M.

DUCT FABRICATION

Fabricate ducts, elbows, transitions, offsets, branch connections, and other construction with galvanized, sheet steel, according to SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."  Comply with requirements for metal thickness, reinforcing types and intervals, tie-rod applications, and joint types and intervals.

Revise pressure classes below to suit Project.  Delete if indicated on Drawings.  Sheet metal contractors will assume a default pressure class of 1-inch wg (250 Pa) if class is not indicated.

Static-Pressure Classifications:  Unless otherwise indicated, construct ducts to the following:

Supply Ducts:  3-inch wg.

Return Ducts:  2-inch wg, negative pressure.

Exhaust Ducts:  2-inch wg, negative pressure.

Cross Breaking or Cross Beading:  Cross break or cross bead duct sides 19 inches and larger and 0.0359 inch thick or less, with more than 10 sq. ft. of unbraced panel area, unless ducts are lined.

Round Supply And Exhaust Fitting Fabrication:  Fabricate 90-degree tees and laterals and conical tees to comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible," with metal thicknesses specified for longitudinal seam straight duct.

Diverging-Flow Fittings:  Fabricate with a reduced entrance to branch taps with no excess material projecting from body onto branch tap entrance.

Elbows:  Fabricate in die-formed, gored, pleated, or mitered construction.  Fabricate bend radius of die-formed, gored, and pleated elbows one and one-half times elbow diameter.  Unless elbow construction type is indicated, fabricate elbows as follows:

Round Elbows, 8 Inches and Smaller:  Fabricate die-formed elbows for 45- and 90-degree elbows and pleated elbows for 30, 45, 60, and 90 degrees only.  Fabricate nonstandard bend-angle configuration or nonstandard diameter elbows with gored construction.

Round Elbows, 9 through 14 Inches:  Fabricate gored or pleated elbows for 30, 45, 60, and 90 degrees, unless space restrictions require a mitered elbow.  Fabricate nonstandard bend-angle configuration or nonstandard diameter elbows with gored construction.

Round Elbows, Larger Than 14 Inches, and All Flat-Oval Elbows:  Fabricate gored elbows, unless space restrictions require a mitered elbow.

EXECUTION

INSTALLATION

Duct installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of ducts, fittings, and accessories.

Construct and install each duct system for the specific duct pressure classification indicated.

Install round ducts in lengths not less than 12 feet, unless interrupted by fittings.

Install ducts with fewest possible joints.

Install fabricated fittings for changes in directions, changes in size and shape, and connections.

Install couplings tight to duct wall surface with a minimum of projections into duct.

Install ducts, unless otherwise indicated, vertically and horizontally, parallel and perpendicular to building lines; avoid diagonal runs.

Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

Install ducts with a clearance of 1 inch, plus allowance for insulation thickness.

Conceal ducts from view in finished spaces.

Coordinate layout with suspended ceiling, fire- and smoke-control dampers, lighting layouts, and similar finished work.

Electrical Equipment Spaces:  Route ductwork to avoid passing through transformer vaults and electrical equipment spaces and enclosures.  No ductwork shall be permitted to pass over any electrical panels.  The space above the electrical panels shall be reserved for electrical work.  This free space shall extend from the top of the electrical panels to the roof.

Non-Fire-Rated Partition Penetrations:  Where ducts pass through interior partitions and exterior walls, and are exposed to view, conceal space between construction opening and duct or duct insulation with sheet metal flanges of same metal thickness as duct.  Overlap opening on four sides by at least 1-1/2 inches.

Fire-Rated Partition Penetrations:  Where ducts pass through interior partitions and exterior walls, install appropriately rated fire damper, sleeve, and firestopping sealant.  Fire and smoke dampers are specified in Division 15 Section "Duct Accessories."

JOINT AND SEAM SEALING

Seam And Joint Sealing:  Seal duct seams and joints according to the duct pressure class indicated and as described in SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."

Pressure Classification Less Than 2-Inch wg:  Transverse joints.

Seal externally insulated ducts before insulation installation.

HANGERS AND SUPPORTS

Install rigid round and rectangular metal ducts with support systems indicated in SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."

Support horizontal ducts within 24 inches of each elbow and within 48 inches of each branch intersection.

Support vertical ducts at a maximum interval of 16 feet and at each floor.

Install concrete inserts before placing concrete.

CONNECTIONS

Connect equipment with flexible connectors according to Division 15 Section "Duct Accessories."

For branch, outlet and inlet connections, comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible."

- END OF SECTION 15815

This Page Left Intentionally Blank