MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16442 - PANELBOARDS

GENERAL

SUMMARY

This Section includes distribution and branch-circuit panelboards that are NOT a part of the package furnished by the Owner’s supplier.

Retain below if Project contains fusible panelboards.

See Division 16 Section "Fuses" for fuses for fusible panelboard switches.

SUBMITTALS

Completed “Conformance Submittal” included with this Section.

Operation and maintenance data.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Comply with NEMA PB 1.

Comply with NFPA 70.

PRODUCTS

MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

Manufacturers:  Subject to compliance with requirements, provide products by the following:

Square D Co.

FABRICATION AND FEATURES

Enclosures: Surface-mounted cabinets.  NEMA PB 1, Type 1, suitable for environmental conditions at installed location.

Delete items below if not applicable.  Add other Project-specific requirements.

Outdoor Locations:  NEMA 250, Type 3R.

Other Wet or Damp Indoor Locations:  NEMA 250, Type 4.

Front:  Hinged front cover with integral panelboard door.  For surface-mounted fronts, match box dimensions; for flush-mounted fronts, overlap box.

Finish:  Manufacturer's standard enamel finish over corrosion-resistant treatment or primer coat.

Directory Card:  With transparent protective cover, mounted in metal frame, inside panelboard door.

Bus: Hard-drawn copper, 98 percent conductivity.

Equipment Ground Bus:  Adequate for feeder and branch-circuit equipment ground conductors;  bonded to box.

Panelboard Short-Circuit Rating:

Select one of two subparagraphs below for series-rated system or system that has panelboards and circuit breakers rated for full value of short-circuit current available at location of equipment.  Edit to suit Project, and coordinate with Drawings.

Fully rated to interrupt symmetrical short-circuit current available at terminals.

Four paragraphs below may be manufacturer's options.  Select those required.  Add other required features and coordinate with Drawings.

Delete paragraph below except if a panelboard incorporates one or more main service disconnect switches.  Edit to suit Project.

Panelboards with Main Service Disconnect:  Listed for use as service equipment.

Delete first paragraph below if future provisions are not required.

Spaces for Future Devices:  Mounting brackets, bus connections, and necessary appurtenances required for future installation of devices.

Skirt for Surface-Mounted Panelboards:  Same gage and finish as panelboard front with flanges for attachment to panelboard, wall, and ceiling or floor.

Feed-through Lugs:  Locate at opposite end of bus from incoming lugs or main device.

LOAD CENTERS

Overcurrent Protective Devices:  Bolt-on, full-module circuit breakers.

LIGHTING AND APPLIANCE BRANCH-CIRCUIT PANELBOARDS

Branch Overcurrent Protective Devices: Bolt-on circuit breakers, replaceable without disturbing adjacent units.

Coordinate below with Drawings.

Doors:  Front mounted with concealed hinges; secured with flush latch with tumbler lock; keyed alike.

DISTRIBUTION PANELBOARDS

Edit this Article to suit Project.  Coordinate with Drawings.

Doors:  Front mounted, and secured with vault-type latch with tumbler lock; keyed alike.

Branch overcurrent protective devices shall be one of the following:

For Circuit-Breaker Frame Sizes 125 A and Smaller: Bolt-on circuit breakers.

For Circuit-Breaker Frame Sizes Larger Than 125 A:  Bolt-on circuit breakers;

OVERCURRENT PROTECTIVE DEVICES

Edit this Article to suit Project.  Coordinate with schedules and Drawings.

Molded-Case Circuit Breaker:  NEMA AB 1, with interrupting capacity to meet available fault currents.

Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

Application Listing:  Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

Shunt Trip:  120-V trip coil energized from separate circuit, set to trip at 75 percent of rated voltage.

EXECUTION

INSTALLATION

Install panelboards and accessories according to NEMA PB 1.1.

Coordinate subparagraph below with Drawings.

Install flush unless otherwise indicated.

Mounting Heights:  Top of trim 74 inches above finished floor, unless otherwise indicated.

Mounting:  Plumb and rigid without distortion of box.  Mount recessed panelboards with fronts uniformly flush with wall finish.

Install filler plates in unused protective device spaces.

Delete paragraph below if ceilings are not accessible.

Revise below if "Balancing Loads" Paragraph is deleted from "Field Quality Control" Article below.

Wiring in Panelboard Gutters:  Arrange conductors into groups and bundle and wrap with wire ties after completing load balancing.

IDENTIFICATION

Identify field-installed conductors, interconnecting wiring, and components; provide warning signs as specified in Division 16 Section "Basic Electrical Materials and Methods."

Panelboard Nameplates:  Label each panelboard with engraved metal or laminated-plastic nameplate mounted with corrosion-resistant screws.

Revise paragraph below if "Balancing Loads" Paragraph is deleted from "Field Quality Control" Article below.

Circuit Directory:  Create a directory to indicate installed circuit loads after balancing panelboard loads.  Obtain approval before installing.  Use a computer or typewriter to create directory;  handwritten directories are not acceptable.

FIELD QUALITY CONTROL

Testing and Inspection:  After installing panelboards and after electrical circuitry has been energized, demonstrate product capability and compliance with requirements.

Test insulation resistance of panelboard bus with a megohmmeter, and ground continuity of cabinet and ground bus.  Reject buses with insulation resistance less than 2 megohms.

Correct defective and malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

Circuit changes made during load balancing may negate color-coding of phases and circuits.  If load balancing proves undesirable or is to be performed by others, delete first paragraph and subparagraphs below.

END OF SECTION 16442

CONFORMANCE SUBMITTAL

# Section 16442 – Panelboards

Lowe’s of _______________________________________________________________________

(City, State)

General Contractor:	________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

Sub-Contractor:		________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

# Product Verification: (Provide for each panelboard Not a part of Owner’s electrical gear package)

Panelboards installed in this store NOT supplied as part of the Owner’s electrical gear package meet the product guidelines of Section 16442 “Panelboards”

Describe where this panel will be located and the loads served: _______________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

General Contractor’s Affidavit:

I represent to Lowe’s that the product selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the project specification.  If noncompliance is discovered the General Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and Lowe’s specifications.  The work shall be completed immediately as directed by Lowe’s without additional cost to Lowe’s and/or the contract.

General Contractor:	________________________________________________________________

(Signature of the Authorized Agent of the General Contractor)			(Date)

________________________________________________________________

(Print Name of the Authorized Agent of the General Contractor)

Sub-Contractor’s Affidavit:

I represent to Lowe’s that the product selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the project specification.  If noncompliance is discovered the Sub-Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and Lowe’s specifications.  The work shall be completed immediately as directed by Lowe’s and/or the General Contractor without additional cost to Lowe’s and/or the contract.

Sub-Contractor:		________________________________________________________________

(Signature of the Authorized Agent of the Sub-Contractor)				(Date)

________________________________________________________________							              (Print Name of the Authorized Agent of the Sub-Contractor)

This Page Left Intentionally Blank