MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16461 - DRY-TYPE TRANSFORMERS (1000 V AND LESS)

GENERAL

SUMMARY

This Section includes dry-type distribution and specialty transformers rated 1000 V and less that are not a part of the package furnished by the Owner’s supplier.

SUBMITTALS

Completed “Conformance Submittal” included with this Section.

Operation and maintenance data, including manufacturer’s shop drawings and wiring schematics.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Comply with NFPA 70.

PRODUCTS

MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

Manufacturers:  Subject to compliance with requirements, provide products by the following:

Square D; Groupe Schneider.

TRANSFORMERS, GENERAL

Description:  Factory-assembled and -tested, air-cooled units of types specified, designed for 60-Hz service.

Cores:  Grain-oriented, nonaging silicon steel.

Edit first paragraph below if copper coils are desired.  Transformers with copper coils cost about 40 percent more and have about 20 percent greater weight than those with aluminum coils.  Enclosures are usually the same size for the same ratings for both coil materials.  Aluminum is the standard coil material for most manufacturers, but most will provide copper coils if specified.  Both types are fitted to connect to circuit conductors of either material.

Coils:  Electrical grade copper.  Continuous windings without splices, except for taps.

Internal Coil Connections:  Brazed or pressure type.

GENERAL-PURPOSE DISTRIBUTION AND POWER TRANSFORMERS

Comply with NEMA ST 20 and list and label as complying with UL 1561.

Cores:  One leg per phase.

Windings:  One coil per phase in primary and secondary.

If all transformers have same enclosure, edit first paragraph below.  If enclosures vary, delete paragraph and show on Drawings.

Enclosure: Indoor, ventilated.

Insulation Class:  185 or 220 deg C class for transformers 15 kVA or smaller; 220 deg C class for transformers larger than 15 kVA.

If all transformers have same insulation temperature rise, select from two subparagraphs below.  If temperature rises vary, delete all and show on Drawings.  See Editing Instruction No. 3 in the Evaluations.

Rated Temperature Rise:  150 deg C maximum rise above 40 deg C, for 220 deg C class insulation; 115 deg C maximum rise for 185 deg C class insulation.

Taps:  For transformers 3 kVA and larger, full-capacity taps in high-voltage windings are as follows:

If all transformers have same voltage taps, select from three subparagraphs below.  If taps vary, delete all and show on Drawings.  First item is standard.

Taps, 3 through 10 kVA:  Two 5-percent taps below rated high voltage.

Taps, 15 through 500 kVA:  Six 2.5-percent taps, 2 above and 4 below rated high voltage.

Retain paragraph and subparagraphs below where some transformers will supply significant nonsinusoidal load current.  Show transformer K-factor ratings on Drawings or in a schedule.  See Evaluations.

K-Factor Rating:  Transformers indicated to be K-factor rated are listed to comply with UL 1561 requirements for nonsinusoidal load current handling capability to the degree defined by the designated K-factor.

Transformer design prevents overheating when carrying full load with harmonic content corresponding to the designated K-factor.

Nameplate states the designated K-factor of the transformer.

Coordinate below with Drawings.

Wall-Mounting Brackets:  Furnished and Installed by the steel erector.

FINISHES

Indoor Units:  Manufacturer's standard paint over corrosion-resistant pretreatment and primer.

EXECUTION

INSTALLATION

Arrange equipment to provide adequate spacing for access and for circulation of cooling air.

Firmly secure transformers by bolting to the floor using minimum ½-inch expansion anchors and ½-inch bolts at each corner of the transformer.

Identify transformers and install warning signs according to Division 16 Section "Basic Electrical Materials and Methods."

FIELD QUALITY CONTROL

Test Objectives:  To ensure transformer is operational within industry and manufacturer's tolerances, is installed according to the Contract Documents, and is suitable for energizing.

Schedule tests and provide notification at least seven days in advance of test commencement.

Tests:  Include the following minimum tests and inspections according to manufacturer's written instructions.  Comply with IEEE C57.12.91 for test methods and data correction factors.

Inspect accessible components for cleanliness, mechanical and electrical integrity, and damage or deterioration.  Verify that temporary shipping bracing has been removed.  Include internal inspection through access panels and covers.

Inspect bolted electrical connections for tightness according to manufacturer's published torque values or, if not available, those specified in UL 486A and UL 486B.

Test Failures:  Compare test results with specified performance or manufacturer's data.  Correct deficiencies identified by tests and retest.  Verify that transformers meet specified requirements.

ADJUSTING

Adjust transformer taps to provide optimum voltage conditions at utilization equipment throughout normal operating cycle of facility.

- END OF SECTION 16461

# CONFORMANCE SUBMITTAL

# Section 16461 – Drytype Transformers

Lowe’s of _______________________________________________________________________

(City, State)

General Contractor:	________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

Sub-Contractor:		________________________________________________________________

(Company Name, Phone Number)

________________________________________________________________

(Address)

# Product Verification:

The transformers installed in this store will meet the product guidelines of Section 16461 “Drytype Transformers”

General Contractor’s Affidavit:

I represent to Lowe’s that the product selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the project specification.  If noncompliance is discovered the General Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and Lowe’s specifications.  The work shall be completed immediately as directed by Lowe’s without additional cost to Lowe’s and/or the contract.

General Contractor:	________________________________________________________________

(Signature of the Authorized Agent of the General Contractor)			(Date)

________________________________________________________________

(Print Name of the Authorized Agent of the General Contractor)

Sub-Contractor’s Affidavit:

I represent to Lowe’s that the product selected will be installed in compliance with the applicable codes for the authorities having jurisdiction and in accordance with the project specification.  If noncompliance is discovered the Sub-Contractor shall make or cause to be made all necessary corrections to meet the applicable codes and Lowe’s specifications.  The work shall be completed immediately as directed by Lowe’s and/or the General Contractor without additional cost to Lowe’s and/or the contract.

Sub-Contractor:		________________________________________________________________

(Signature of the Authorized Agent of the Sub-Contractor)				(Date)

________________________________________________________________						                	(Print Name of the Authorized Agent of the Sub-Contractor)

This Page Left Intentionally Blank